## PSH
Storage pumped hydro - hybrid PSH (combined)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 300 | 300 | 300 | 300 | 100 | 500 | 100 | 500 | A | 1
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 100 | 4000 | 100 | 4000 |  | 1
Electricity efficiency, net, name plate | % | 80 | 80 | 80 | 80 | 70 | 82 | 70 | 82 |  | 2, 3
Electricity efficiency, net, annual average | % | 80 | 80 | 80 | 80 | 70 | 82 | 70 | 82 |  | 2, 3
Forced outage | % | 4 | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 3
Planned outage | % | 5.8 | 5.8 | 5.8 | 5.8 | 2 | 11.5 | 2 | 11.5 |  | 3
Technical lifetime (years) | years | 50 | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 4
Construction time (years) | years | 5 | 5 | 5 | 5 | 2.5 | 7.5 | 2.5 | 7.5 | B | 5
Space requirement | 1000 m2/MWe | 30 | 30 | 30 | 30 | 15 | 45 | 15 | 45 | B, C | 5
Ramping configuration
Ramping | % per minute | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 3, 6
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
Warm start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Cold start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Economic data
Specific investment | MUSD/MW | 0.75 | 0.75 | 0.75 | 0.74 | 0.55 | 6 | 0.55 | 5.95 | D, E, F, G | 1
- of which equipment | % | 30 | 30 | 30 | 30 | 20 | 50 | 20 | 50 | D, E | 7
- of which installation | % | 70 | 70 | 70 | 70 | 50 | 80 | 50 | 80 | D, E | 7
- of which equipment | MUSD/MW | 0.23 | 0.22 | 0.22 | 0.22 | 0.11 | 3 | 0.11 | 2.98 | D, E | 7
- of which installation | MUSD/MW | 0.53 | 0.52 | 0.52 | 0.52 | 0.28 | 4.8 | 0.27 | 4.76 | D, E | 7
Fixed O&M | USD/MW-year | 15000 | 14963 | 14911 | 14879 | 6875 | 150000 | 6819 | 148786 | H | 4
Variable O&M | USD/MWh | 1.4 | 1.4 | 1.4 | 1.4 | 0.5 | 3 | 0.5 | 2.98 |  | 5, 7
Technology specific data
Size of reservoir | MWh | 6000 | 6000 | 6000 | 6000 | 3000 | 20000 | 3000 | 20000 | I | 1
Load/unload time | hours | 5 | 5 | 5 | 5 | 4 | 12 | 4 | 12 | I | 1
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | J
Notes:
A | Size per turbine.
B | Uncertainty (Upper/Lower) is estimated as +/- 50%.
C | Space requirements for new sites is highly uncertain given the geographical dependency.
D | Numbers are very site sensitive to geographical characteristics. There will be a limited improvement by learning curve development, but best, i.e. cheap locations will be utilized first. The investment largely depends on civil work.
E | Cost are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2025, with Stated Policies Scenario (STEPS) for the central values and Current Policies Scenario (CPS) and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
F | Cost uncertainties in the short and long term indicate the spread of cost based on the examined cases. Costs are highly uncertain given the geographical characteristics.
G | Based on an open loop system (hybrid PSH).
H | Fixed O&M is assumed to be between 1% and 2.5%/year depending on the size of the plant in line with [4] with the central value to be approx. 1.25% for a plant at 1000 MW.
I | The size of the total power plant and not per unit (turbine).
J | Assuming a closed system with negligible water losses. Evaporation losses may occur as described under Hydro Power in the TC for power generation.
References
1 | Data from projects in Viet Nam
2 | NREL Annual Technology Baseline (ATB), 2025
3 | U.S. Department of Energy, 2015, “Hydropower Market Report”
4 | U.S. Department of Energy, 2022 - 2022 Grid Energy Storage Technology Cost and Performance Assessment
5 | Danish Energy Agency, Ea Energy Analyses, Technology Data for the Indonesian Power Sector, 2024
6 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition"
7 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower"

## Lithium ion battery
Storage utility scale Li-Ion
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Form of energy stored |  | Electricity
Application |  | System, power- and energy-intensive
Energy storage capacity for one unit | MWh | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B, C
Output capacity for one unit | MW | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B, C
Input capacity for one unit | MW | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | A, B, C
Storage capacity | MWh | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B, C
Discharge time | hours | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | A, B, C
Round trip efficiency | %AC | 91 | 92 | 92 | 92 |  |  |  |  | D | 1, 3, 4, 6
Round trip efficiency | %DC | 95 | 96 | 96 | 96 |  |  |  |  | D | 1, 3, 4, 6
- Charging efficiency | % | 98 | 98 | 98.5 | 98.5 | [5 empty] | 7
- Discharge efficiency | % | 97 | 97 | 97.5 | 97.5 | [5 empty] | 7
Self-discharge rate | %/day | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | E | 9
Forced outage | % | 0.38 | 0.35 | 0.3 | 0.25 |  |  |  |  | F
Planned outage | % | 0.38 | 0.38 | 0.19 | 0.19 |  |  |  |  | F
Technical lifetime | cycles | 5000 | 6000 | 12000 | 20000 | [5 empty] | 1, 3
Technical lifetime | years | 15 | 20 | 30 | 30 |  |  |  |  | G | 1, 3, 10
Construction time | years | 0.25 | 0.2 | 0.2 | 0.2 |  |  |  |  | H
Ramping configuration
Response time from idle to full-rated discharge | s | 0.08 | 0.08 | 0.08 | 0.08 |  |  |  |  | I | 11
Response time from full-rated charge to discharge | s | 0.08 | 0.08 | 0.08 | 0.08 |  |  |  |  | I | 11
Economic data
Specific investment | MUSD/MWh | 0.36 | 0.24 | 0.2 | 0.18 | 0.28 | 0.45 | 0.14 | 0.25 | J | 1, 12, 13, 14, 15
- energy component | MUSD/MWh | 0.128 | 0.07 | 0.05 | 0.04 | 0.1 | 0.17 | 0.03 | 0.07 | K
- power component | MUSD/MW | 0.116 | 0.08 | 0.07 | 0.07 | 0.1 | 0.14 | 0.06 | 0.09 | K, L | 16
- other project costs | MUSD/MWh | 0.203 | 0.16 | 0.14 | 0.13 | 0.15 | 0.25 | 0.09 | 0.16 | K, M
Fixed O&M | USD/MW-year | 12000 | 9269 | 8035 | 7592 | 10000 | 32000 | 6327 | 20245 | N | 1
Variable O&M | USD/MWh | 2 | 1.54 | 1.34 | 1.27 | 2 | 2.6 | 1.27 | 1.64 | O | 1, 17
Technology specific data
Energy storage expansion cost | MUSD/MWh | 0.33 | 0.24 | 0.2 | 0.19 | 0.25 | 0.38 | 0.14 | 0.21 | P
Power expansion cost | MUSD/MW | 0.12 | 0.09 | 0.08 | 0.07 | 0.1 | 0.13 | 0.06 | 0.08 | Q
Alternative Total investment cost | MUSD/MW | 1.44 | 1.04 | 0.87 | 0.81 | 1.1 | 1.65 | 0.62 | 0.93
Energy density | kWh/m3 | 100 | 110 | 130 | 150 |  |  |  |  | R | 18, 19
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | -
Notes:
A | One unit is defined as a 20 feet container including LIB system and excluding power conversion system. The Specific investment cost under Economic data is the total cost for a 4MWh/1MW BESS, which is the typical size of grid-scale BESS in 2025. (Some specific BESS might have lower energy capacity and higher power capacity or vice versa).
B | A 4-hour battery has been picked as a reference, as there is more data available for this power-to-energy ratio in the references listed.
C | Power and energy output can be scaled linearly by utilizing many modules (up to 250 MW has been demonstrated (https://www.pv-magazine-australia.com/2023/08/10/battery-capacity-overtakes-pumped-hydro-in-nem/). Output capacity expansion can be done reprograming the management unit without any new battery module. For Utility batteries the ratio between energy storage and capacity is in general between 1 and 10 (C-rate between 1/10 and 1), only rarely the ration will be below 1.
D | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore, the average DC roundtrip efficiency is expected to increase slightly. . The AC roundtrip efficiency includes losses in the power electronics and is 2-4 % lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80 % and 90 % [1,8].
E | Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0,05% and 0,20% a day in 2025 and are expected to stay flat to 2050.
F | The main source of outage of the battery cells is caused by extreme heat or cold as this may push the cells beyond their operational limits. However, these are considered rare events and for many system may never occur. Outages may however happen due to the power electronic or thermal management which will also need yearly maintenance causing planned outage. In total this is expected to remain below a few days per year and is unlikely to change significantly over time.
G | Samsung SDI 2016 whitepaper on ESS solutions provide 15-year lifetime for current modules operating at C/2 to 3C. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
H | Construction time of a BESS varies widely from site to site. Construction of the BESS system alone may only take a few months, but getting approval to connect to the grid and potential upgrade to the grid may delay start of operations by as much as 18 months [4]. However, this may differ significantly from country to country.
I | The response time is obtained from simulated response time experiments with hardware in the loop [13].
J | The specific investment cost is the total cost of a 4 MWh/1 MW BESS, which is the typical grid-scale battery. However, size and Power to Energy ratio may vary significantly from system to system and must be calculated based on the expected system specifications.
K | A learning rate of 24 % is assumed for the energy component, 12 % for the power component and 10 % for other costs, according to BNEF [14][15] and IEA [6].
L | Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years.
M | Other costs include construction costs and entrepreneur work. These costs are heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore, other costs are assumed to roughly correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.
N | Fixed O&M is assumed to be 3 $/kW-year in 2025 based on [1].
O | Cost per MWh of energy discharged from the battery.
P | Since multi-MWh LIB systems are modularly scalable, the energy storage expansion cost is here estimated to be equal to the energy component plus 20% of the respective “other costs”.
Q | Since multi-MW LIB systems are modularly scalable, the capacity expansion cost equals the capacity component cost plus 20% of the respective “other costs”.
R | Energy density is reported at container/enclosure level (nominal kWh divided by container volume based on external dimensions). It includes space for internal equipment and auxiliaries and is not cell/pack/rack-level.
References
1 | Lazard, Lazard's Levelized Cost of Storage (2025)
2 | NREL, W. Cole et al., 2025 - Cost Projections for Utility-Scale Battery Storage: 2025 Update
3 | TESvolt. TPS-E Technical datasheet, (2024). https://www.tesvolt.com/_media/05%20SERVICE/03%20Downloads/E-Serie/TPS-E/Datenblatt/RD.TI.094.E.en-US_v.B.02.pdf
4 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
5 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
6 | IEA, Battery and Secure Energy Transitions, part of World Energy Outlook 2023, April 2024
7 | Samsung SDI; ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, 2018, http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf; Smart Battery Systems, 2016, https://www.samsungsdi.com/upload/ess_brochure/SamsungSDI_ESS_201609EN.pdf
8 | A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
9 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020
10 | BYD. 20 Ft ESS ,model CS20H-B2982-E-R1M01, (2024). http://www.bydenergy.com/productDetail?locale=EN&type=CN&name=20ft%20ESS&id=77&pageContentType=PRODUCT_CATEGORY_ENERGY
11 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
12 | V. Ramasamy, J. Zuboy, E. O’Shaughnessy, D. Feldman, J. Desai, M. Woodhouse, P. Basore and R. Margolis, "U.S. Solar Photovoltaic System and Energy Storage Cost Benchmarks, With Minimum Sustainable Price Analysis: Q1 2022.," National Renewable Energy Laboratory, Golden, CO, 2022
13 | BloombergNEF, "Lithium-Ion Battery Pack Prices Hit Record Low of $139/kWh," 26 November 2023. [Online]. Available: https://about.bnef.com/blog/lithium-ion-battery-pack-prices-hit-record-low-of-139-kwh/. [Accessed 19 August 2024]
14 | BloombergNEF, "2025 Lithium-Ion Battery Price Survey", 2025 update
15 | BloombergNEF, "Energy Storage System Cost Survey", 2025 update
16 | Pacific Northwest National Laboratory, "2022 Grid Energy Storage Technology Cost and Performance Assessment," U.S. Department of Energy, 2022
17 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596
18 | Sungrow Power Supply Co., Ltd., 2023 – PowerTitan 2.0 Liquid Cooled Energy Storage System: ST5015kWh-2500kW-2h / ST5015kWh-1250kW-4h (Version 3). Online: https://cdn.enfsolar.com/z/pp/2024/3/eg31o40cy48s9un7k/ds-20230925-st5015kwh-2500kw-2h-1250kw-4h-v3-en.pdf
19 | Sunwoda Energy – BESS Container NoahX ¦ Sunwoda Energy. Online: https://www.sunwodaenergy.com/electric/bess-container-noahx.html

## Vanadium Redox Battery
Vanadium Redox Battery (VRB)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Form of energy stored |  | Electricity
Application |  | System, power- and energy-intensive
Energy storage capacity for one unit | MWh | 0.5 | 0.6 | 0.65 | 0.75 | 0.5 | 0.7 | 0.7 | 0.8 | A, Q | 1, 2, 3, 4
Output capacity for one unit | MW | 0.25 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 | A, Q | 1, 2, 3, 4
Input capacity for one unit | MW | 0.25 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.4 | 0.6 | A, Q | 1, 2, 3, 4
Round trip efficiency | %DC | 78 | 80 | 83 | 85 | 75 | 85 | 80 | 90 | B | 1, 2, 3, 4
- Charge efficiency | % | - | - | - | - | - | - | - | -
- Discharge efficiency | % | - | - | - | - | - | - | - | -
Energy losses during storage | %/day | 0.25 | 0.2 | 0.15 | 0.1 | 0.15 | 0.25 | 0.05 | 0.15 | C | 1, 2, 3, 4
Forced outage | % | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.1 | 0.4 | D, Q | 1, 2, 3, 4
Planned outage | % | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.05 | 0.2 | D, Q | 1, 2, 3, 4
Technical lifetime | years | 25 | 30 | 35 | 40 | 25 | 35 | 30 | 50 |  | 1, 2, 3, 4, 5, 6
Construction time | years | 0.5 | 0.25 | 0.2 | 0.15 | 0.15 | 0.5 | 0.1 | 0.2 | E, Q | 7
Ramping configuration
Response time from idle to full-rated discharge | s | 0.2 | 0.1 | 0.1 | 0.1 | 0.05 | 0.25 | 0.05 | 0.2 | F, G | 8
Response time from full-rated charge to full-rated discharge | s | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 | F, G, Q | 8
Economic data
Specific investment | MUSD/MWh | 0.72 | 0.74 | 0.53 | 0.43 | 0.63 | 0.89 | 0.25 | 0.52 | H | 7, 8, 9, 10, 11
- energy component | MUSD/MWh (or %) | 0.26 | 0.19 | 0.1 | 0.06 | 0.15 | 0.26 | 0.04 | 0.09 | H, I | 7, 8, 9, 10, 11
- power component | MUSD/MW (or %) | 0.51 | 0.45 | 0.34 | 0.31 | 0.38 | 0.51 | 0.2 | 0.34 | H, J | 7, 8, 9, 10, 11
- other project costs | MUSD/MWh (or %) | 0.2 | 0.18 | 0.17 | 0.16 | 0.18 | 0.19 | 0.09 | 0.18 | H, K | 7, 8, 9, 10, 11
Fixed O&M | USD/MW/year | 5369 | 5521 | 3954 | 3225 | 3133 | 8856 | 1003 | 5234 | H, L | 7, 8, 9, 10, 11
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | M | 7, 8, 9, 10, 11
Technology specific data
Energy storage expansion cost | MUSD/MWh | 0.27 | 0.2 | 0.11 | 0.07 | 0.16 | 0.27 | 0.41 | 0.16 | H, N | 7, 8, 9, 10, 11
Power expansion cost | MUSD/MW | 0.54 | 0.47 | 0.36 | 0.34 | 0.41 | 0.54 | 0.2 | 0.54 | H, O | 7, 8, 9, 10, 11
Lifetime in total number of cycles | None | >20,000 | >40,000 | 100000 | >100,000 | 20000 | 40000 | 40000 | 200000 | P | 8
Specific power | W/kg | 8.25 | 16.5 | 16.5 | 16.5 | 8.25 | 16.5 | 8.25 | 16.5 | A, Q | 8
Power density | W/m3 | 3704 | 7407 | 7407 | 7407 | 3704 | 8889 | 3704 | 8889 | A, Q | 8
Specific energy | Wh/kg | 16.5 | 19.7 | 23.4 | 24.6 | 16.5 | 24.6 | 23 | 26.25 | A, Q | 8
Energy density | Wh/m3 | 7407 | 8880 | 9996 | 11111 | 7407 | 11111 | 10370 | 11852 | A, Q | 8
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | -
Notes:
A | One unit defined as a 40 feet ISO container including VRFB system (cell stacks, electrolyte tanks, and control system) and excluding power conversion system. Based on data from existing and/or available VRFB systems.
B | Efficiency varies considerably between different VRFBs, depending on control system and use cases.
C | Energy losses depend on idle situation. If pumps are off and electrolyte not present in the reaction stack no energy loss occurs. This increases response time (see below). Self-discharge only occurs for electrolyte inside the reaction stack. This is a relatively small volume and the self-discharge will be at most 1% for 40ft unit. Losses related to stand-by energy consumption of pumps are not included.
D | Some companies guarantee at least 99.5% uptime.
E | Depends highly on the installation.
F | Time is less than 100 ms for idle situation with electrolyte in reaction stack and pumps on [4]. Less than 1 s if electrolyte must first be pumped [5]. Less than 1 min if pumps are not on [5]. PCS might be limiting the response time.
G | Might in practice be limited by PCS.
H | Valid for installations with rated discharge times of 2 hours. This relates to a C-rate 1.0 for a 40ft unit system (i.e., 250 kW with 500 kWh). The price development is strongly dependent on competition with other energy storage technologies as a high market share will be needed to reach a low cost.
I | Composed of electrolyte and tank infrastructure for a unit system cost at around 250 USD/kWh.
J | Composed of stack and other power capacity related cost of about 1175 USD/kW for the 40ft unit system.
K | Other costs include construction costs and entrepreneur work. These costs are heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore, other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature.
L | Fixed O&M is assumed to be constant at around 1% for a 2 to 8h system. O&M depends on the energy to power ratio. Most suppliers define O&M below 15% of Capex over lifetime of > 20 years.
M | Variable O&M is assumed to be 0 USD/MWh, as a fixed use pattern is assumed throughout the VRFB calendar life, and all replacement and maintenance is accounted for under fixed O&M.
N | Since multi-MWh VRFB systems are modular and scalable, the energy storage expansion cost is basically electrolyte cost plus the required tank infrastructure and the cost in MUSD/MWh will therefore decrease with longer storage durations.
O | Since multi-MW VRFB systems are modular and scalable, the capacity expansion cost equals the stack system component cost plus required installation material and the specific investment cost in MUSD/MWh will therefore decrease with larger capacities.
P | Cyclic lifetime of up to 200.000 cycles has already been demonstrated for VRFBs, but might still require refurbishment in practical operation.
Q | Uncertainties are based on a qualified guess for VRFB, based on their scientific principles.
References
1 | Sumitomo RFB LDES Brochure 07/2024; https://sumitomoelectric.com/sites/default/files/2024-09/download_documents/RFB_Catalog_EN%EF%BC%88A4%EF%BC%89_202407.pdf [Accessed: October 2024]
2 | Invinity VS3-022 VRFB Datasheet 01/2023; https://invinity.com/wp-content/uploads/2023/03/Invinity-VS3-022-Vanadium-Flow-Battery-Data-Sheet-MAR00016-2023-01.pdf?_gl=1*6s9c22*_up*MQ..*_gs*MQ..&gclid=Cj0KCQiAr7C6BhDRARIsAOUKifiHvGiiyTULQ-gUOYdt_TJ75bBrWYg0OeP9FpZ-cYuakmLoFT8shogaAit5EALw_wcB [Accessed: October 2024]
3 | Enerox CellCube Series Release 4.2 Datasheet 06/2023; https://cellcube.com/wp-content/uploads/Cellcube-Datasheet-ACDC.pdf [Accessed: October 2024]
4 | VisBlue VisFlow 60 Datasheet; https://www.visblue.com/product/visflow60 [Accessed: October 2024]
5 | IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017
6 | Sterner, Stadler; Handbook of energy Storage; 2019; https://doi.org/10.1007/978-3-662-55504-0
7 | “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017]
8 | Maria Skyllas-Kazacos et. al.; Flow Batteries: From Fundamentals to Applications; 2023; DOI:10.1002/9783527832767
9 | Internal database at the Danish Technological Institute, based on existing realized VRFB projects
10 | K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017
11 | The Storage Future Study (SFS) by the National Renewable Energy Laboratory (NREL); https://www.nrel.gov/analysis/storage-futures.html [Accessed: January 2025]

## Hydrogen storage
Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy storage capacity for one unit | MWh | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 |  | 1
Output capacity for one unit | MW | - | - | - | - | - | - | - | - | A
Input capacity for one unit | MW | 0 | 0 | 0 | 0 | 0.1 | 0.99 | 0 | 0 | B | 1, 2
Round trip efficiency | % | 88 | 89 | 90 | 90 | 88 | 88 | 90 | 90 | C | 1
- Charge efficiency | % | 88 | 89 | 90 | 90 | 88 | 88 | 90 | 90 | D
- Discharge efficiency | % | ~100 | ~100 | ~100 | ~100 | ~100 | ~100 | ~100 | ~100 | E
Energy losses during storage | % / period | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | F
Auxiliary electricity consumption (only for heat and gas storage) | % of output | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | J
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I
Planned outage | weeks per year | 3 | 2 | 1.5 | 1 | 3 | 3 | 1.5 | 0.5 | G | 3
Technical lifetime | years | 25 | 30 | 30 | 30 | 25 | 25 | 30 | 30
Construction time | years | 0.5 | 0.4 | 0.4 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 |  | 3
Regulation ability (Only for electricity storage)
Primary regulation | % per 30 sec | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | H | 3
Secondary regulation | % per minute | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | H | 3
Economic data
Specific investment | MUSD/MWh | 0.085 | 0.067 | 0.04 | 0.031 | 0.085 | 0.085 | 0.053 | 0.031 |  | 1
Compressor component | MUSDMWh | 0.045 | 0.034 | 0.017 | 0.011 | 0.045 | 0.045 | 0.022 | 0.011 |  | 1
Type I tanks component | MUSD/MWh | 0.027 | 0.022 | 0.015 | 0.013 | 0.027 | 0.027 | 0.02 | 0.013 |  | 1
Installation, equipment, manhours | MUSD/MWh | 0.013 | 0.011 | 0.009 | 0.007 | 0.013 | 0.013 | 0.01 | 0.007 |  | 1
Fixed O&M | USD/MW/year | 895 | 746 | 746 | 597 | 895 | 895 | 672 | 448 |  | 1
Variable O&M | USD/MWh | - | - | - | - | - | - | - | -
Technology specific data
Gravimetric energy density | kWh/kg | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
Volumetric energy density @0oC and 1atm pressure | kWh/m3 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
Permeation characteristics for Type I tanks | mol/s/m/Mpa1/2 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 | 2,84×10-27 |  | 3
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | -
Notes:
A | Cannot be defined since there is no conversion of hydrogen back to electricity in the form of a fuel cell in the system
B | The only power input that is considered is the input for the compressor and does not include power needs for the electrolyser that is making the hydrogen as described in the system definition. Compressor power input decrease of 5% every 10 years
C | Calculated in the "Energy Efficiency" section. Compressor efficiency linearly improved by 20% until 2050.
D | The charge efficiency is practically the round-trip efficiency itself as there are almost no losses in the discharge process (See note E)
E | Almost no losses during discharge as it is a physical discharge for a pressurized gas from a valve.
F | Permeation characteristics are negligible for Type I tanks, see also Technology specific data.
G | System O&M includes maintenance of the compressor and periodic check of the tanks integrity.
H | System complies with the frequency regulation requirements from Energinet
I | No hydrogen storage systems are known to have time of forced outage.
J | Compressor consumption is not considered auxiliary. Rest of losses that can be translated into energy losses and consequently more electricity consumption are negligible.
References
1 | M. Kraglund, “Alkaline membrane water electrolysis with non-noble catalysts,” Technical University of Denmark, 2017.
2 | J. Jonas, “THE HISTORY OF HYDROGEN”.
3 | N. T. Stetson, S. McWhorter, and C. C. Ahn, Introduction to hydrogen storage, vol. 2006. Elsevier Ltd., 2015.

## Compressed Air Energy Storage
Compressed Air Energy Storage
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy storage capacity for one unit | MWh | 3000 | 3000 | 3000 | - | - | 3000 | 10000 | A
Output capacity for one unit | MW | 300 | 300 | 300 | - | - | 300 | 500 | A
Input capacity for one unit | MW | 60 | 60 | 60 | - | - | 60 | 80 | A
Round trip efficiency | % | 60 | 70 | 72 | 55 | 55 | 64 | 72 | A, B, C
- Charge efficiency | % | 80 | 84 | 85 | 80 | 80 | 80 | 85 | A
- Discharge efficiency | % | 80 | 84 | 85 | 69 | 69 | 80 | 85 | A
Energy losses during storage | % / period | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Auxiliary electricity consumption | % of output | - | - | -
Forced outage | % | 5 | 4 | 4 | - | - | 2 | 4 | A
Planned outage | weeks per year | 5 | 4 | 3 | - | - | 2 | 3 | A, B
Technical lifetime | years | 40 | 40 | 40 | 35 | 45 | 35 | 45 | A, B
Construction time | years | < 3 | < 3 | < 3 | 2 | 3 | 2 | 3 | A
Regulation ability
Idle to full discharge | sec | 700 | 1000 | 1000 | 500 | 1000 | 800 | 1,200 | A, D, E
Full charge to full discharge | sec | - | - | - |  |  |  |  | F
Economic data
Specific investment | MUSD/MWh | 0.13 | 0.13 | 0.11 |  |  |  |  | A | 1, 2, 3
- Energy component | % | 40 | 40 | 40 |  |  |  |  | G | 2
- Capacity component | % | 50 | 50 | 50 | [5 empty] | 2
- Other project costs | % | 10 | 10 | 10 | [5 empty] | 2
Fixed O&M | USD/kW/year | 18.4 | 18.4 | 18.4 | [5 empty] | 1, 2, 3
Variable O&M | USD/MWh | 1.7 | 1.7 | 1.7 | [5 empty] | 1, 2, 3
Technology specific data
Energy storage expansion cost | MUSD/MWh | 0.065 | 0.065 | 0.055 |  |  |  |  | H
Output capacity expansion cost | MUSD/MW | 0.065 | 0.065 | 0.055 |  |  |  |  | H
Notes:
A | The starting values are from the Danish TC, adjusted using the references (if present in the column).
B | For efficiency it is assumed that that new CAES plants can be constructed with at least the same efficiency as the McIntosh plant.
C | The use of gas in a CAES plant is assumed at the same efficiency as the average use of chemical fuels in the Danish electricity system, i.e. 35% in 2014.
D | The obtainable ramping rate is likely to decrease after application of thermal energy storage. This is because the heat must be delivered to the storage material, which is a process that cannot be controlled independently.
E | If a CAES plant is operated as a hot spinning reserve, it can reach the maximum capacity within a few minutes. The emergency startup times from cold conditions at the Huntorf and McIntosh plants are about 5 minutes. Their normal startup times are about 10 to 12 minute.
F | Operation not suitable nor relevant for CAES. Data not available.
G | Energy component here taken as the cavern excavating.
H | Compressed air energy storage is considered a scalar system and therefore the energy and output capacity expansion costs are here estimated to be equal to the energy and output capacity components plus the “other costs”.
References
1 | IEA, "Energy Storage Technology Roadmap, Technology Annex, p. 5,", March 2014
2 | "InflationData.com", InflationData, 2017. [Online]. [Accessed March 2017]
3 | E. Drury, P. Denholm and R. Sioshansi, "The Value of Compressed Air Energy Storage in Energy and Reserve Markets," National Renewable Energy Laboratory, USA, 2009

## Flywheel
Flywheels
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Energy storage capacity for one unit | MWh | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | A, B
Output capacity for one unit | MW | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | A, B
Input capacity for one unit | MW | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | A, B
Round trip efficiency | % | 98 | 98 | 98 | 98 | 99 | 98 | 99 | A, B
- Charge efficiency | % | 99 | 99 | 99 | 99 | 99.5 | 99 | 99.5 | A, B
- Discharge efficiency | % | 99 | 99 | 99 | 99 | 99.5 | 99 | 99.5 | A, B
Energy losses during storage | %/day | 3 | 1 | 1 | 2 | 5 | 0.5 | 1.5 | A, C
Auxiliary electricity consumption | % of output
Forced outage | %
Planned outage | weeks per year
Technical lifetime | years | 20 | 25 | 25 | 20 | 25 | 20 | 25 | A, D
Construction time | years | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | A, B
Regulation ability
Response time from idle to full-rated discharge | sec | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | A, B
Response time from full-rated charge to full-rated discharge | sec | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | A, B
Economic data
Specific investment | MUSD/MWh | 21.8 | 20.4 | 19.7 |  |  |  |  | A | 1, 2, 3
- Energy component | % | 98.5 | 98.5 | 98.5 |  |  |  |  | A, B
- Capacity component | % | 1.5 | 1.5 | 1.5 |  |  |  |  | A, B
Fixed O&M | USD/MW/year | 7.1 | 7.1 | 7.1 | [5 empty] | 3
Variable O&M | USD/MWh | 0.4 | 0.4 | 0.4 | [5 empty] | 3
Technology specific data
Specific energy | Wh/kg | 350 | 350 | 350 | 300 | 400 | 350 | 400 | A, B
Specific energy | Wh/l | 1500 | 1500 | 1500 | 1300 | 2000 | 1300 | 2000 | A, B
Cycle life | cycles | 350000 | 350000 | 350000 |  |  |  |  | B
Water consumption | L/MWh | 0 | 0 | 0
Notes:
A | The starting values are from the Danish Technology Catalogue, adjusted using the references (if present in the column).
B | Data informed by WattsUp Power February 2018.
C | Loss per day measured by WattsUp Power. The projected losses towards 2050 is justified by results already now obtained by NASA.
D | +25 years on mechanics. 15 years on electronics. Informed by WattsUp Power March 2017.
References
1 | S. o. A. E. I. SAE, "https://global.ihs.com/doc_detail.cfm?rid=GS&&item_s_key=00138611," IHS Markit, 2013. [Online]. [Accessed March 2017]
2 | "Electrical Energy Storage," International Electrotechnical Commission, Geneva, Switzerland, 2011
3 | W. Torell, "Lifecycle Carbon Footprint Analysis of Batteries vs. Flywheels, White Paper 209," Schneider Electric, 2015
4 | "Lazard´s levelized cost of storage - Version 2.0," Lazard, 2016

## Electrolyser-AEC
Hydrogen production with Alkaline Electrolysis (AEC)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Form of energy stored | None
Application | None
Input capacity for one unit | MW input_e
Output capacity for one unit (hydrogen) | kgH2/day max
Input capacity for total plant | MW input_e | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Output capacity for total plant (hydrogen) | kgH2/day max | 46656 | 49379 | 51885 | 55556 | 49037 | 44496 | 56845 | 54323 | A, B
Input
Electricity | % total input (MWh/MWh) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Electricity consumption (stack level) | kWh/kgH2 | 51.4 | 48.6 | 46.3 | 43.2 | 48.9 | 53.9 | 42.2 | 44.2 | C, D | 1, 2, 3, 4
Electricity consumption (stack+BOP level) | kWh/kgH2 | 56.7 | 53.6 | 51 | 47.6 | 53.9 | 59.4 | 46.5 | 48.7 | E | 1, 2, 3, 4
Water for electrolysis | kg/MWh input_e | 175 | 185 | 195 | 208 | 166.9 | 183.9 | 213 | 204
Output
Hydrogen (% total input_e) | % total input_e (MWh/MWh) | 58.7 | 62.2 | 65.3 | 69.9 | 61.7 | 56 | 71.6 | 68.4 | F
Delta E from HHV to LHV (% total input_e) | % total input_e (MWh/MWh) | 11.9 | 12.6 | 13.2 | 14.1 | 12.5 | 11.3 | 14.4 | 13.8 | G, H
Heat loss (% total input_e) | % total input_e (MWh/MWh) | 29.4 | 25.3 | 21.5 | 15.9 | 26 | 32.5 | 14 | 17.8
- hereof unrecoverable heat loss | %-points of heat loss | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | I
- recoverable for district heating | % points of heat loss | 26.4 | 22.3 | 18.5 | 12.9 | 23 | 29.5 | 11 | 14.8
Hydrogen | kg/MWh input_e | 19.4 | 20.6 | 21.6 | 23.1 | 20.4 | 18.5 | 23.7 | 22.6
Forced outage | % | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | J
Planned outage | days per year | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | J
Technical lifetime | years | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | J
Frequency of stack replacement [h] |  | 80000 | 92500 | 94500 | 101500 | 70500 | 89500 | 83000 | 120000 | C, D, K | 1, 2, 3, 4, 5
Construction time | years | 2 | 2 | 2 | 2 | 1.5 | 2 | 1.5 | 2 | L
Economic data
Specific investment | USD/kW of total input_e | 1175 | 750 | 575 | 400 | 950 | 1400 | 350 | 475 | D, M, N, X | 2, 4, 5, 6, 7, 8, 9, 10
Specific investment | USD/kgH2/day max output | 2518 | 1519 | 1108 | 720 | 1937 | 3146 | 616 | 874 | A, B, O
- hereof equipment | % | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | J, P
- hereof installation | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | J, P
Fixed O&M | % of specific investment/y | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | J, Q | 8
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | R
Technology specific data
Current density | A/cm2 | 0.8 | 1 | 1.2 | 1.5 | 0.5 | 0.8 | 1.2 | 1.5 | J, S | 8
Cold start up time | min from 0 to 100% | 60 | 30 | <30 | <30 | 38 | 79 | <30 | <30 | T | 3, 8, 11
Stack size | MW | 5 | 5 | 10 | 10 | 3.8 | 6.3 | 10 | 10 | J | 3, 10, 12
Degradation rate | %/1000h | 0.13 | 0.12 | 0.11 | 0.1 | 0.11 | 0.15 | 0.09 | 0.11 | J, S, U | 5, 8
Plant footprint | m2/MW input_e | 184 | 108 | 90 | 72 | 147 | 276 | 57 | 108 | V, W
Water consumption | L/MWh | 670 | 670 | 670 | 670 | - | - | - | - |  | 13
Notes:
A | For the unit regarding "day" a 100% load factor is assumed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily full load hours may vary and should therefore be adjusted for.
B | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
C | The values were derived from multiple sources. 2040 were calculated using linear regression based on the data provided in the mentioned references, encompassing the years 2030 and 2050.
D | Upper and lower values are based on the average of the standard deviations found in the relevant data as shown in note C. Standard deviations for specific investments follow expected values from typical pre-FEED projects (20%).
E | Based on reference [3], the energy consumption of the entire system (including both stack and balance of plant components) is estimated.
F | Efficiency for AEC and PEMEC is calculated based on the electricity consumption of the stack and BOP level, and assuming the LHV of hydrogen.
G | The HHV electrolyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
H | The calculation is based on the HHV and LHV of hydrogen.
I | 3% of the energy is estimated to be unrecoverable for AEC and PEMEC hydrogen plants.
J | Based on internal projects and references performed at Ramboll including FEED projects and estimations from clients and from suppliers.
K | Values have been rounded to nearest 500.
L | It is estimated internally at Ramboll that construction for 1 MW and 10 MW H2 plants will take 0.75-1 years, 100 MW H2 plants will take 1.5-2 years, and 1 GW H2 plants will take >3 years. This estimate includes large electrical components and the plant itself.
M | Investment costs for 100 MW of all technologies are based on public CAPEX estimates for 2030 and 2050. 2020 projects at Ramboll have then been used to find the progression by size.
N | Values have been rounded to nearest 25.
O | To analyse the cost breakdown of a hydrogen plant, the electrolyser unit and the Balance of the Plant (BOP) are considered. Additionally, various other cost factors that are essential for the plant commissioning are taken into account, such as civil work, installation, and Engineering, Procurement, and Construction (EPC) expenses.
P | For H2 plants sized 1 MW and 10 MW, estimated cost ratio of equipment to installation is 95:5, and for H2 plants sized 100 MW and 1 GW, the estimated cost ratio of equipment to installation is 90:10.
Q | Stack replacement costs are not included.
R | The price of the input streams (water and electric energy), has not been estimated.
S | The values are based on public sources. Approaching 2050 yields is a higher margin of uncertainty.
T | The operational flexibility of a system is often determined by its cold start-up time, which represents the most time-consuming step and serves as a crucial distinguishing factor between different technologies.
U | The provided degradation rate of the electrolyser stack is an average value. However, it is important to note that this rate is also influenced by the operation profile, such as the frequency of start/stop operations.
V | The size of the electrolyser unit is determined based on a multistack configuration, using benchmarking data sourced from Ramboll. For example, the assumptions for 10 MW electrolysis for PEMEC, AEC and SOEC were 2 x 5 MW stacks inside one container, 2 x 2.5 MW stacks inside one container, needing two containers, and 72 x 0.14 MW containers, respectively.
W | The plant footprint includes the installation of electrolyser units, each with their respective rectifiers. A safety distance of 5 m is maintained between each unit, and a designated laydown area is provided for maintenance operations. BOP is also included in the total footprint value.
X | The data presented here includes the electrolyser unit, electrolyser system (excl. electrolyser unit cost), balance of the plant (BOP), control system, civil infrastructure and indirect costs such as EPC expenses. The data does not include compressors, hydrogen storage nor power connection in the form of step-down transformers and further switchgears. However, initial rectifiers and transformers for the electrolysers at site are included.
References
1 | DNV, “Hydrogen Forecast to 2050”, 2022.
2 | Monitor Deloitte, “Fueling the Future of Mobility: Hydrogen Electrolysers”, 2021.
3 | IRENA, Making the breakthrough: Green hydrogen policies and technology costs, Abu Dhabi, 2021.
4 | IEA, “The Future of Hydrogen, Seizing today's opportunities, Executive summary, and recommendations, Report prepared by the IEA for the G20, Japan,” IEA, 2019.
5 | DoE Hydrogen and Fuel Cell Technologies Office, “Technical Targets for Liquid Alkaline Electrolysis,” DoE, [Accessed July 2023].
6 | IRENA, “Green Hydrogen Cost Reduction: Scaling up electrolysers to meet the 1.5°C climate goal,” International Renewable Energy Agency, Abu Dhabi, 2020.
7 | IEA, “Global Hydrogen Review 2023,” 2023.
8 | Clean Hydrogen Partnership, Strategic Research and Innovation Agenda 2021-2027, 2022.
9 | ISPT, “Gigawatt green hydrogen plant; State-of-the-art design and total installed capital costs,” 2020.
10 | Fraunhofer Institute for Solar Energy Systems, “COST FORECAST FOR LOW-TEMPERATURE ELECTROLYSIS,” 2021.
11 | Janke et.al., “Optimizing power-to-H2 participation in the Nord Pool electricity market: Effects of different bidding strategies on plant operation,” Renewable Energy, vol. 156, pp. 820-836, August 2020.
12 | Böhm et.al., “Projecting cost development for future large-scale power-to-gas implementations by scaling effects,” Applied Energy, vol. 264, 15 April 2020.
13 | IRENA and Bluerisk, 2023 - Water for Hydrogen Production

## Electrolyser-PEMEC
Hydrogen production with PEMEC
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Form of energy stored | None
Application | None
Input capacity for one unit | MW input_e
Output capacity for one unit (hydrogen) | kgH2/day max
Input capacity for total plant | MW input_e | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Output capacity for total plant (hydrogen) | kgH2/day max | 44566 | 47398 | 49909 | 53791 | 46013 | 43207 | 57143 | 50811 | A, B
Input
Electricity | % total input (MWh/MWh) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Electricity consumption (stack level) | kWh/kgH2 | 53.9 | 50.6 | 48.1 | 44.6 | 52.2 | 55.5 | 42 | 47.2 | C, D | 1, 2, 3, 4
Electricity consumption (stack+BOP level) | kWh/kgH2 | 60.5 | 56.9 | 54.1 | 50.2 | 58.6 | 62.4 | 47.2 | 53.1 | E | 1, 2, 3, 4
Water for electrolysis | kg/MWh input_e | 167 | 178 | 187 | 202 | 162 | 172.5 | 214 | 191
Output |  | 0
Hydrogen (% total input_e) | % total input_e (MWh/MWh) | 55 | 58.5 | 61.6 | 66.4 | 57.9 | 52.3 | 70.5 | 62.7 | F
Delta E from HHV to LHV (% total input_e) | % total input_e (MWh/MWh) | 11.3 | 12 | 12.7 | 13.7 | 11.7 | 11 | 14.5 | 12.9 | G, H
Heat loss (% total input_e) | % total input_e (MWh/MWh) | 33.7 | 29.5 | 25.7 | 19.9 | 31.8 | 35.4 | 15 | 24.4
- hereof unrecoverable heat loss | %-points of heat loss | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | I
- recoverable for district heating | % points of heat loss | 30.7 | 26.5 | 22.7 | 16.9 | 28.8 | 32.4 | 12 | 21.4
Hydrogen | kg/MWh input_e | 18.6 | 19.7 | 20.8 | 22.4 | 19.2 | 18 | 23.8 | 21.2
Forced outage | % | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | J
Planned outage | days per year | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | J
Technical lifetime | years | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 | J
Frequency of stack replacement [h] |  | 65500 | 77500 | 90000 | 105000 | 55000 | 76000 | 86500 | 123500 | C, D, K | 1, 2, 3, 4, 5
Construction time | years | 2 | 2 | 2 | 2 | 1.5 | 2 | 1.5 | 2 | L
Economic data (in USD2025)
Specific investment | USD/kW of total input_e | 1325 | 875 | 675 | 475 | 1050 | 1600 | 375 | 575 | D, M, N, X | 2, 4, 5, 6, 7, 8, 9, 10
Specific investment | USD/kgH2/day max output | 2973 | 1846 | 1352 | 883 | 2282 | 3703 | 656 | 1132 | A, B, O
- hereof equipment | % | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | J, P
- hereof installation | % | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | J, P
Fixed O&M | % of specific investment/y | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | J, Q | 8
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | R
Technology specific data
Current density | A/cm2 | 2.8 | 5 | 7.5 | 10 | 1.5 | 3 | 7.5 | 12.5 | J, S | 8
Cold start up time | min from 0 to 100% | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 1 | 0.1 | 0.3 | T | 3, 8, 11
Stack size | MW | 1.5 | 2 | 5 | 10 | 1 | 1.3 | 10 | 10 | J | 3, 10, 12
Degradation rate | %/1000h | 0.17 | 0.13 | 0.1 | 0.1 | 0.19 | 0.25 | 0.1 | 0.11 | J, S, U | 5, 8
Plant footprint | m2/MW input_e | 77 | 45 | 37 | 28 | 61 | 115 | 22 | 42 | V, W
Water consumption | L/MWh | 526 | 526 | 526 | 526 | - | - | - | - |  | 13
Notes:
A | For the unit regarding "day" a 100% load factor is assumed here (Where the system is operated at nominal capacity all 24 hours of the day). In operation the daily full load hours may vary and should therefore be adjusted for.
B | Maximum hydrogen output per day, assuming 24 hours of full load operation in a day.
C | The values were derived from multiple sources. 2040 were calculated using linear regression based on the data provided in the mentioned references, encompassing the years 2030 and 2050.
D | Upper and lower values are based on the average of the standard deviations found in the relevant data as shown in note C. Standard deviations for specific investments follow expected values from typical pre-FEED projects (20%).
E | Based on reference [3], the energy consumption of the entire system (including both stack and balance of plant components) is estimated.
F | Efficiency for AEC and PEMEC is calculated based on the electricity consumption of the stack and BOP level, and assuming the LHV of hydrogen.
G | The HHV electrolyser efficiency can be calculated as the sum of the rows: "ΔE from HHV to LHV" and "Hydrogen".
H | The calculation is based on the HHV and LHV of hydrogen.
I | 3% of the energy is estimated to be unrecoverable for AEC and PEMEC hydrogen plants.
J | Based on internal projects and references performed at Ramboll including FEED projects and estimations from clients and from suppliers.
K | Values have been rounded to nearest 500.
L | It is estimated internally at Ramboll that construction for 1 MW and 10 MW H2 plants will take 0.75-1 years, 100 MW H2 plants will take 1.5-2 years, and 1 GW H2 plants will take >3 years. This estimate includes large electrical components and the plant itself.
M | Investment costs for 100 MW of all technologies are based on public CAPEX estimates for 2030 and 2050. 2020 projects at Ramboll have then been used to find the progression by size.
N | Values have been rounded to nearest 25.
O | To analyse the cost breakdown of a hydrogen plant, the electrolyser unit and the Balance of the Plant (BOP) are considered. Additionally, various other cost factors that are essential for the plant commissioning are taken into account, such as civil work, installation, and Engineering, Procurement, and Construction (EPC) expenses.
P | For H2 plants sized 1 MW and 10 MW, estimated cost ratio of equipment to installation is 95:5, and for H2 plants sized 100 MW and 1 GW, the estimated cost ratio of equipment to installation is 90:10.
Q | Stack replacement costs are not included.
R | The price of the input streams (water and electric energy), has not been estimated.
S | The values are based on public sources. Approaching 2050 yields is a higher margin of uncertainty.
T | The operational flexibility of a system is often determined by its cold start-up time, which represents the most time-consuming step and serves as a crucial distinguishing factor between different technologies.
U | The provided degradation rate of the electrolyser stack is an average value. However, it is important to note that this rate is also influenced by the operation profile, such as the frequency of start/stop operations.
V | The size of the electrolyser unit is determined based on a multistack configuration, using benchmarking data sourced from Ramboll. For example, the assumptions for 10 MW electrolysis for PEMEC, AEC and SOEC were 2 x 5 MW stacks inside one container, 2 x 2.5 MW stacks inside one container, needing two containers, and 72 x 0.14 MW containers, respectively.
W | The plant footprint includes the installation of electrolyser units, each with their respective rectifiers. A safety distance of 5 m is maintained between each unit, and a designated laydown area is provided for maintenance operations. BOP is also included in the total footprint value.
X | The data presented here includes the electrolyser unit, electrolyser system (excl. electrolyser unit cost), balance of the plant (BOP), control system, civil infrastructure and indirect costs such as EPC expenses. The data does not include compressors, hydrogen storage nor power connection in the form of step-down transformers and further switchgears. However, initial rectifiers and transformers for the electrolysers at site are included.
References
1 | DNV, “Hydrogen Forecast to 2050”, 2022
2 | Monitor Deloitte, “Fueling the Future of Mobility: Hydrogen Electrolysers”, 2021
3 | IRENA, Making the breakthrough: Green hydrogen policies and technology costs, Abu Dhabi, 2021.
4 | IEA, “The Future of Hydrogen, Seizing today's opportunities, Executive summary, and recommendations, Report prepared by the IEA for the G20, Japan,” IEA, 2019
5 | DoE Hydrogen and Fuel Cell Technologies Office, “Technical Targets for Liquid Alkaline Electrolysis,” DoE, [Accessed July 2023]
6 | IRENA, “Green Hydrogen Cost Reduction: Scaling up electrolysers to meet the 1.5°C climate goal,” International Renewable Energy Agency, Abu Dhabi, 2020
7 | IEA, “Global Hydrogen Review 2023,” 2023
8 | Clean Hydrogen Partnership, Strategic Research and Innovation Agenda 2021-2027, 2022
9 | ISPT, “Gigawatt green hydrogen plant; State-of-the-art design and total installed capital costs,” 2020
10 | Fraunhofer Institute for Solar Energy Systems, “COST FORECAST FOR LOW-TEMPERATURE ELECTROLYSIS,” 2021
11 | Janke et.al., “Optimizing power-to-H2 participation in the Nord Pool electricity market: Effects of different bidding strategies on plant operation,” Renewable Energy, vol. 156, pp. 820-836, August 2020
12 | Böhm et.al., “Projecting cost development for future large-scale power-to-gas implementations by scaling effects,” Applied Energy, vol. 264, 15 April 2020
13 | IRENA and Bluerisk, 2023 - Water for Hydrogen Production

## Green ammonia
Green Ammonia plant: Hydrogen to ammonia (excl. electrolyser and excl. ASU)
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size | TPD | 229 | 458 | 2290 |  |  |  |  | A
Typical total plant size (Ammonia output) | MW | 50 | 100 | 500
Inputs
N2 Consumption | t/t ammonia | 0.84 | 0.84 | 0.84 | 0.82 | 0.86 | 0.82 | 0.86 | B, L
Hydrogen Consumption | t/t ammonia | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | B, L
Hydrogen Consumption | MWh/MWh total inputs | 0.95 | 0.95 | 0.95 | 0.93 | 0.97 | 0.93 | 0.97 | B, L
Electricity Consumption | MWh/MWh total inputs | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.04 | 0.08 | C, L
Outputs
Ammonia Output | MWh/MWh total inputs | 0.82 | 0.82 | 0.82 | 0.81 | 0.84 | 0.81 | 0.84
High value heat | MWh/MWh total inputs | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | D, L
Heat loss | MWh/MWh total inputs | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.03 | 0.04 | E, L
Forced outage, unplanned shutdown | % | 5 | 3 | 2 | 2 | 8 | 2 | 4 | M
Planned outage | Weeks per year | 3 | 3 | 3 |  |  |  |  | M
Operation capacity | % | 20-100 | 20-100 | 20-100 |  |  |  |  | N
Technical lifetime | years | 30 | 30 | 30
Construction time | years | 2 | 2 | 2
Economic data
Specific investment | MUSD/MW ammonia output | 2.33 | 1.9 | 1.2 | 1.82 | 3.07 | 0.84 | 1.4 | F, I, J, M
- equipment | % | 50 | 50 | 50 |  |  |  |  | M
- installation | % | 50 | 50 | 50 |  |  |  |  | M
Fixed O&M | kUSD/MW ammonia/year | 56 | 46 | 29 | 44 | 73 | 20 | 34 | G, M
Variable O&M | USD/MWh ammonia | 0.03 | 0.03 | 0.03 | 0.01 | 0.06 | 0.01 | 0.06 | H, M
Start up | MUSD/1,000t ammonia | - | - | -
Technology specific data
Specific investment mark-up factor optional ASU |  | 1.09 | 1.09 | 1.09 | 97% | 100% | 97% | 100% | F, M
Specific energy content | GJ/ton ammonia | 18.9 | 18.9 | 18.9
Specific density | kg/l or ton/m3 ammonia | 626 | 626 | 626
Specific investment | MUSD/TPD ammonia output | 0.51 | 0.42 | 0.26 | 0.4 | 0.67 | 0.18 | 0.3 | F, I
Fixed O&M | MUSD/TPD ammonia | 15.3 | 12.5 | 7.8 | 11.9 | 20.1 | 5.5 | 9.1
Variable O&M | USD/t ammonia | 0.15 | 0.15 | 0.15 | 0.07 | 0.29 | 0.07 | 0.29
Start up | MUSD/TPD ammonia | - | - | -
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | - | K
Notes:
Performance and cost data are given for the ammonia synthesis only. An indication of the cost and energy requirements of the ASU is given in the chapter as well, but it is held separate from the synthesis. Cost and performance data for the electrolysis are given in a separate chapter and datasheet within this Technology Catalogue and are meant to be combined, when evaluating the whole production path-way.
A | Typical NH₃ plant size based on H2 supply from 100 MWe electrolyser for 2020.
B | Assuming 98% efficiency with respect to mass of the ammonia synthesis
C | Assumption of higher-pressure electrolysis available in the future, requiring lower compression power. A green ammonia plant that contains a dedicated ASU for nitrogen production will have additional power requirements
D | Steam at up to 350 °C may be produced by NH3 synthesis
E | Heat available at 30-60°C
F | Specific investment of green NH₃ plant (excl. electrolysis, excl. ASU, NH₃ storage and utilities) is estimated as 54% of conventional NH₃ plant based on NG. Cost is decreasing with time mainly because of scale effect (increasing plant size). To add the cost of an ASU a multiplication factor of 1.06-1.09 should be applied to the total Specific Investment (both entries in Economic data and Technology-specific data) as a rule of thumb.
G | G: Fixed O&M is taken as 3% of CAPEX
H | Variable O&M estimated as cost for catalyst replacement and misc. consumables
I | Economic data is given in 2025-$
J | Cost projection is considering economy of scale only and does not consider further technical development, due to the maturity of ammonia synthesis. In case capacities are expected for other years than shown in the datasheet, one should use the corresponding cost data of the respective capacity instead of the cost data for a given year. See also Figure 16 in the chapter.
K | When the electrolysis process is excluded, the water consumption is negligible.
L | Based on calculated mass and energy balance
M | Based on collected data, i.e. based on several sources, as specified in the qualitative section
N | Based on normal operation ranges for instrumentations and rotating equipment. Lower capacity range is possible but it is normally expensive as spare instrumentation and rotating equipment is required

## E-methanol
E-methanol (excl. electrolyser)
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical plant size | ton-methanol/day | 300 | 600 | 1200 |  |  |  |  | A | 1
Typical total plant size | MW methanol output | 69 | 138 | 276
Inputs
CO2 | ton/ton-methanol | 1.4 | 1.4 | 1.4 | 1.4 | 1.5 | 1.4 | 1.5 | B | 2
Hydrogen | ton/ton-methanol | 0.19 | 0.19 | 0.19 | 0.2 | 0.2 | 0.2 | 0.2 | C | 2
Hydrogen | MWh/ton-methanol | 6.4 | 6.4 | 6.4 | 6.4 | 7 | 6.4 | 7 | D
Electricity | MWh/ton-methanol | 0.1 | 0.1 | 0.1 | 0.08 | 0.12 | 0.08 | 0.12 | E | 2
Net steam | MWh/ton-methanol | 0.58 | 0.58 | 0.58 | 0.46 | 0.7 | 0.46 | 0.7 | F | 2
Outputs
Methanol | MWh/MWh total input | 0.78 | 0.78 | 0.78 | 0.78 | 0.858 | 0.78 | 0.858 | G
Heat loss; usable as low-temp. heat | MWh/MWh total input | 0.2 | 0.2 | 0.2 | 0 | 0.22 | 0 | 0.22 | H
Additional heat loss | MWh/MWh total input | 0.02 | 0.02 | 0.02 | 0.018 | 0.022 | 0.018 | 0.022 | I
Water | ton/ton-methanol | 0.55 | 0.55 | 0.55 | 0.55 | 0.605 | 0.55 | 0.605 | J
Forced outage | % | 5 | 3 | 2
Planned outage | weeks per year | 3 | 3 | 3
Technical lifetime | years | 30 | 30 | 30
Construction time | years | 2 | 2 | 2 |  |  |  |  | K
Economic data
Specific investment | MUSD/ton-methanol/day | 0.38 | 0.31 | 0.25 | 0.19 | 0.57 | 0.12 | 0.37 | L, O, P | 3
Specific investment | MUSD/MW methanol output | 1.65 | 1.33 | 1.06 | 0.83 | 2.48 | 0.53 | 1.6 | O, P
- equipment | % | 75 | 75 | 75
- installation | % | 25 | 25 | 25
Fixed O&M | kUSD/ton-methanol/day/year | 11 | 8.6 | 7.4 |  |  |  |  | M
Fixed O&M | kUSD/MW methanol/year | 48 | 37 | 32
Variable O&M | USD/ton-methanol | 33 | 33 | 33 |  |  |  |  | N | 3
Variable O&M | USD/MWh methanol | 6 | 6 | 6
Start-up | MUSD/ton/day-methanol | - | - | -
Technology specific data
Water consumption (L/MWh) |  | 0 | 0 | 0 | - | - | - | - | Q
Notes:
A | In the period 2020-2030 the plant size is governed by the available carbon resource. Towards 2050, direct air capture is expected to play a role resulting in increased plant sizes.
B | The value is slightly higher than stoichiometric reaction due to the formation of organic by-products.
C | Calculated based on 2,130 Nm3-H2/ton-methanol and 0,09 kg-H2/Nm3-H2.
D | Converted based on a lower heating value for hydrogen of 33,3 kWh/kg.
E | Haldor Topsøe [5] states a value of 500 kWh/ton-methanol, which includes compression of H2 and CO2. The figure provided in the table covers electricity demand for auxiliary equipment excl. compressors and is assumed to be 20 % of the value provided by Haldor Topsøe.
F | Steam produced in the methanol reactor is reused for heating purposes in the distillation section. The value provided states the net import steam.
G | Calculated based on a lower heating value for methanol of 19,9 GJ/ton.
H | Based on assumption that warm streams can be cooled to 50 °C.
I | Includes heat loss to ambient and cooling at temperatures below 50 °C.
J | Based on stoichiometry of the chemical reaction. The waste water includes traces of organic byproducts from the methanol synthesis, and can be handled in conventional central waste water facilities or treated on site.
K | Construction time from order placement to start of commercial operation. Methanol reactor is a long lead item which is a governing factor for the construction time.
L | According to battery limits as described in the text. Reduction in specific investment over time is due to economy of scale and not due to technological development.
M | Estimated to be 3 % of CAPEX.
N | Excludes costs related to process inputs such as steam, electricity, hydrogen and carbon dioxide.
O | Included in the CAPEX data are the: Methanol reactor incl. catalyst, Methanol distillation for achieving grade AA methanol, Piping between components inside the battery limits (ISBL), Electrical cabling on low voltage side, SCADA (Supervisory Control And Data Acquisition), Methanol tank which is assumed to contain one day’s production, Distillation columns prepared for utilization of district heating (higher temperatures of cooling water).
P | Excluded from the CAPEX data are the: H2 and CO2 compressors, Electrical transformers, High voltage electrical systems, Fee to DSO for connecting to electrical grid, Utility systems: cooling system, steam boiler, Possible connection to district heating system, Treatment of purge gases and separated by-products, Contingencies, Cost of land, VAT and taxes and Owners costs.
Q | When the electrolysis process is excluded, the water consumption is negligible.
References
1 | Lemvig Biogas, "Erfaringer med totrins udrådning i fuldskala hos Lemvig Biogasanlæg," [Online]. Available: https://www.biogas.dk/wp-content/uploads/2021/12/Lars-A-Kristensen_Lemvig-Biogas_21-12-08.pdf
2 | Haldor Topsøe, [Online]. Available: https://info.Topsøe.com/hubfs/DOWNLOADS/DOWNLOADS%20-%20Brochures/eMethanol.pdf?hsCtaTracking=6ca24cee-0aed-45df-8aa4-846ecd19151c%7C5d9f6bef-ebfc-483e-8a06-cdfed4aee34a
3 | H. Nami, G. Butera, N. J. B. Campion, H. L. Frandsen and P. V. Hendriksen, "MarE-fuel: Energy efficiencies in synthesising green fuels and their expected cost," 2021

## Bio methanol
Bio-methanol
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total plant size | 1000t methanol/year | 100 | 200 | 300 | 50 | 200 | 150 | 375 | A, B | 3, 4, 5
Typical total plant size | MW | 65 | 130 | 195 | 33 | 130 | 98 | 244 | A, A1, B | 3, 4, 5
Inputs
Feedstock Consumption | MWh/MWh total input | 1 | 1 | 1 | 0.9 | 1.5 | 0.9 | 1.2 |  | 1
Outputs
Methanol Output | MWh/MWh total input | 0.58 | 0.61 | 0.65 | 0.58 | 0.77 | 0.65 | 0.86 | D | 1
Heat loss; usable as low-temp. heat | MWh/MWh total input | 0.22 | 0.22 | 0.22 | 0.18 | 0.28 | 0.18 | 0.28 | D | 1
Additional heat loss | MWh/MWh total input | 0.22 | 0.22 | 0.22 | 0.18 | 0.28 | 0.18 | 0.28 | D | 1
Electricity Output | MWh/MWh total input | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | D | 1
Forced outage | % | 4 | 0 | 0
Planned outage | weeks per year | 2 | 2 | 2
Technical lifetime | years | 20 | 20 | 20
Construction time | years | 2.5 | 2.5 | 2.5
Economic data (in USD2025)
Specific investment | MUSD/MW methanol | 7.44 | 4.13 | 2.07 | 3.72 | 7.44 | 1.65 | 2.48 | F | 1, 3, 4, 5
- equipment | % | 75 | 75 | 75
- installation | % | 25 | 25 | 25
Fixed O&M | MUSD/MW/year methanol | 0.083 | 0.055 | 0.055 | 0.07 | 0.09 | 0.05 | 0.06 | E, F | 1
Variable O&M | USD/MWh methanol | 28.9 | 19.2 | 19.2 | 25.98 | 31.75 | 17.32 | 21.17 | E, F | 1
Start-up | MUSD/1000t methanol | - | - | -
Technology specific data
Specific energy content | GJ/ton-methanol | 20.1 | 20.1 | 20.1
Specific density | kg/l or ton/m3 | 0.79 | 0.79 | 0.79
Specific investment | MUSD/1000t methanol | 4.83 | 2.69 | 1.34 | 50% | 100% | 80% | 120% | F | 3, 4, 5
Fixed O&M | MUSD/1000t methanol | 0.054 | 0.036 | 0.036 | 90% | 110% | 90% | 110% | E, F | 1
Variable O&M | MUSD/1000t methanol | 0.161 | 0.107 | 0.107 | 90% | 110% | 90% | 110% | E, F | 1
Start-up | MUSD/1000t methanol | - | - | -
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | The plant size range is assumed based on the proposed Värmlands plant and the NREL nth plant.
A1 | This value is the hourly rating and has been calculated as if the unit produces at capacity and was in operations 8,000 h/year.
B | Feedstock availability is likely to determine the maximum plant size.
C | Some plants may produce their own power and have no power imports.
D | Plants that produce their own power will have much lower heat loss.
E | Assumed a 25/75 split on fixed to variable operating costs.
F | MUSD/kton is million USD per 1,000 tons.
References
1 | Andersson, J.,Lundgren, J., and Marklund, M. 2014. Methanol production via pressurized entrained flow biomass gasification – Techno-economic comparison of integrated vs. stand-alone production, In Biomass and Bioenergy, Volume 64, 2014, Pages 256-268, ISSN 0961-9534, https://doi.org/10.1016/j.biombioe.2014.03.063
2 | T Tarud, J., & Phillips, S., Technoeconomic Comparison of Biofuels: Ethanol, Methanol, and Gasoline from Gasification of Woody Residues (Presenta tion) (No. NREL/PR-5100-52636). National Renewable Energy Lab, Golden, CO (United States) 2011. https://www.nrel.gov/docs/fy12osti/52636.pdf
3 | Clausen, L. R., Integrated torrefaction vs. external torrefaction–A thermodynamic analysis for the case of a thermochemical biorefinery. Energy, 77, 597-607, 2014
4 | Värmlands Metanol AB. http://www.varmlandsmetanol.se/Om%20Projektet.htm
5 | Värmlands Metanol AB, Metanol från skog - ett miljövänligt drivmedel, 2016. http://www.varmlandsmetanol.se/dokument/Fol der%20VM%20sept%202016.pd

## Biogas plant Basic plant
Biogas plant Basic plant - 3000 Nm3 CH4/h.
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical capacity | mill. tons biomass input/year | 0.6 | 0.6 | 0.6 | 0.54 | 0.65 | 0.54 | 0.65 | A, B | 1
Typical total plant size | MW output | 29.63 | 29.63 | 29.63 |  |  |  |  | R | 1, 2
Inputs
Biomass | mill. tons/year | 0.6 | 0.6 | 0.6 |  |  |  |  | B | 1
Aux. Electricity | % of output energy | 2.34 | 2.03 | 1.84 | 1.75 | 2.92 | 1.38 | 2.31 | C | 1
Aux. Electricity | kWh/ton input | 10.19 | 8.87 | 8.05 | 7.64 | 12.74 | 6.04 | 10.06 | C | 1
Aux. process heat | % of output energy | 6.87 | 5.97 | 5.42 | 5.84 | 7.9 | 4.61 | 6.24 | D | 1
Aux. process heat | kWh/ton input | 29.96 | 26.07 | 23.67 | 25.47 | 34.46 | 20.12 | 27.22 | D | 1
Outputs
Biogas | % | 100 | 100 | 100 | [5 empty] | 1
Biogas | GJ/ton input | 1.59 | 1.59 | 1.59 |  |  |  |  | R | 1
Biogas production | MJ/s | 29.63 | 29.63 | 29.63 | [5 empty] | 1, 2
Forced outage | % | - | - | - | [5 empty] | 1
Planned outage | days per year | - | - | - | [5 empty] | 1
Technical lifetime | years | 20 | 20 | 20 | 15 | 25 | 15 | 25 | E | 1
Construction time | years | 2 | 2 | 2 | 1 | 3 | 1 | 3 | F, Q
Economic data
Specific investment | mill. USD/MW output | 1.33 | 1.16 | 1.05 | 1.41 | 1.9 | 0.93 | 1.18 | G, H, I, J, N, O, P | 1
- of which equipment | mill. USD/MW output | 1.06 | 0.93 | 0.84 | 1.13 | 1.52 | 0.74 | 0.95 | G, H, I, J
- of which installation | mill. USD/MW output | 0.27 | 0.23 | 0.21 | 0.28 | 0.38 | 0.19 | 0.24 | G, H, I, J
Total O&M | kUSD/MW/year | 98.67 | 85.84 | 77.95 | 83.87 | 113.47 | 72.38 | 92.03 | G, H, I, L | 1
Total O&M | USD/ton-input/year | 4.91 | 4.27 | 3.88 | 4.17 | 5.65 | 3.57 | 4.54 | G, H, I, K, P, N | 1
- of which O&M, excl el. and heat | USD/ton-input/year | 3.28 | 2.86 | 2.59 |  |  |  |  | G, H, I, K | 1
- of which electricity | USD/ton-input/year | 0.88 | 0.76 | 0.69 |  |  |  |  | G, H, I, P | 1
- of which heat | USD/ton-input/year | 0.75 | 0.65 | 0.59 |  |  |  |  | G, H, I, N | 1
Technology Specific data
Hourly gas output | k Nm3 CH4/h | 2.97 | 2.97 | 2.97 | [5 empty] | 1, 3
Yearly gas output | mill. Nm3 CH4/year | 26.05 | 26.05 | 26.05 | [5 empty] | 1, 3
HRT | days | 65 | 65 | 65 | [5 empty] | 1, 2
DS | % | 16 | 16 | 16 |  |  |  |  | M | 1, 2
Methane emission | % of output | 0.9 | 0.9 | 0.9 |  |  |  |  | N | 4, 1
CO2 ressource | mill. Nm3 CO2/year | 19.23 | 19.23 | 19.23 | [5 empty] | 1
CO2 ressource | kton/year | 37.96 | 37.96 | 37.96
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | In the uncertainty calculations, the capacity varies with +/- 10%. This is the biogas plant size for which it is assessed the data can be representative with a similar feedstock input.
B | The biogas input is based on table 5 in the qualitative description, also inserted in datasheet.
C | The uncertainty calculations varies the demand with +/- 25%.
D | The uncertainty calculations varies the demand with +/- 15%.
E | The uncertainty calculation varies the lifetime of the plant by 5 years.
F | The uncertainty calculation varies the construction time of the plant by 1 year.
G | The forecasted prices are based on a learning curve of 10%, this is further elaborated upon in the qualitative description.
H | Due to current supply bottlenecks it is assumed that the price will not develop towards 2025.
I | For uncertainty calculations for 2020 the prices varies by 15%.
J | For uncertainty calculations for 2050 the learning curve for the forecast of prices in 2050 is tested with a 5% learning curve and a 15% learning curve.
K | Equipment is estimated to constitute 80% of the total investment while installation constitute 20%. All costs are without costs for biomass and transport.
L | HRT=Hydraulic Retention Time. The HRT is between 60 and 100 days in newer Danish plants, depending on the biomass input and the plant’s technical specifications.
M | DS%=dry solid content. The biogas plants should be operated with a DS content of a max of 13-14% in the reactor.
N | Due to the warmer climate in Viet Nam, it is assumed that the heat demand required to heat up the digester in a biogas plant is 20% lower than in Denmark, thus lowering the operation and maintenance costs compared to [19]".
O | Production costs are calculated to be planned in 2020 and put into operation in 2022. In bare-field plants, everything is established simultaneously.
P | The cost of feedstocks and transport are not included in the OPEX as they are highly dependent on local conditions and may vary widely. It is, however, important to include costs for feedstock when calculating the operational cost of biogas plants. Pre-treatment of the biomass is included in the costs. It is assumed that the plant uses grinding and milling as mechanical pre-treatment methods for e.g., straw.
Q | Estimated based construction time for similar plants.
R | The gas output per feedstock is estimated in table 35 in the chapter.
References
1 | DGC & PlanEnergi, “Production of upgraded biogas - optimising costs and climate impact - EUDP-j.nr. 64018-0512,” DGC, Hørsholm, 2020
2 | Interview with biogas Denmark (Frank Rosager), 2022, 30/10/2022
3 | The Danish Energy Agency, “Biomasseopgørelsen (Excel fil),” 2022. [Online]. Available: https://ens.dk/ansvarsomraader/bioenergi/energiafgroeder-til-biogas
4 | Rambøll, en: Targeted efforts to reduce methane emissions from Danish biogas plants, Original title (in Danish): “Målrettet indsats for at mindske metantab fra danske biogasanlæg,” Energistyrelsen, 2021

## Biogas upgrading
Biogas upgrading - Amine scrubber (3,000 Nm3/h)
|  | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Typical total size | MW output | 29.34 | 29.34 | 29.34 | [5 empty] | 1
Typical total size | k Nm3 biogas/h | 2.97 | 2.97 | 2.97 | [5 empty] | 1
Capacity | k Nm3 biomethane/h | 2.94 | 2.94 | 2.94 | [5 empty] | 1
Capacity - yearly biomethane production | mill. Nm3 biomethane/h | 25.8 | 25.8 | 25.8 | [5 empty] | 1
Inputs
Biogas | % of biogas input | 100 | 100 | 100 | [5 empty] | 1
Auxilliary electricity for upgrading | % of biogas input | 1.92 | 1.5 | 1.17 | 1.44 | 2.4 | 1.46 | 1.46 | A | 1
Heat | % of biogas input | 10.48 | 8.17 | 6.39 | 8.91 | 12.05 | 7.35 | 7.35 | B | 1
Outputs
Biomethane | % of methane input | 99.05 | 99.05 | 99.05 | [5 empty] | 1
Waste gas | % of methane input | 0.95 | 0.95 | 0.95 | [5 empty] | 1
Waste heat | % of methane input | 5.24 | 5.24 | 5.24 | [5 empty] | 1
Forced outage | weeks per year | 0.29 | 0.29 | 0.29 | [5 empty] | 1
Planned outage | weeks per year | 0.29 | 0.29 | 0.29 | [5 empty] | 1
Technical lifetime | years | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
Construction time | years | 1 | 1 | 1 | 1 | 2 | 1 | 2 | D | 1
Economic data (in USD2025)
Specific investment, upgrading and methane reduction | kUSD/MW output | 248.51 | 193.84 | 151.59 | 211.24 | 285.79 | 183.9 | 119.29 | E, F, G | 1, 2
Fixed O&M | kUSD/MW output/year | 42.35 | 33.03 | 25.83 | 35.99 | 48.7 | 31.34 | 20.33 | E, F, G | 1, 2
- of which fixed O&M costs upgrading and methane reduction, excl. el. and heat | kUSD/MW output/year | 11.85 | 9.25 | 7.23 |  |  |  |  | E, F, G | 1
- of which fixed O&M costs for heat | kUSD/MW output/year | 15.84 | 12.35 | 9.67 |  |  |  |  | E, F, G | 1
- of which fixed O&M costs for el. | kUSD/MW output/year | 14.65 | 11.42 | 8.93 |  |  |  |  | E, F, G | 1
Variable O&M | USD/GJ input | 1.49 | 1.16 | 0.91 | 1.27 | 1.71 | 1.1 | 0.71 | E, F, G | 1
- of which electricity | USD/GJ input | 0.46 | 0.36 | 0.28 | 0.39 | 0.53 | 0.34 | 0.22 | E, F, G | 1
Technology specific data
Methane slip / emission | % | 0.1 | 0,10 | 0.1 | [5 empty] | 1, 3
Minimum load | % of full load | 50 | 50 | 50 | [5 empty] | 1
CO2 ressource | mill. Nm3/year | 19.23 | 19.23 | 19.23 | [5 empty] | 1
CO2 ressource | kton/year | 37.96 | 37.96 | 37.96 | [5 empty] | 1
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | The uncertainty calculations varies the demand with +/- 25%.
B | The uncertainty calculations varies the demand with +/- 15%.
C | The uncertainty calculation varies the lifetime of the plant by 5 years.
D | The uncertainty calculation varies the construction time of the plant by 1 year.
E | The forecasted prices are based on a learning curve of 15%, this is further elaborated upon in the qualitative description.
F | For uncertainty calculations for 2020 the prices varies by 15%.
G | For uncertainty calculations for 2050 the learning curve for the forecast of prices in 2050 is tested with a 10% learning curve and a 20% learning curve.
References
1 | DGC & PlanEnergi, “Production of upgraded biogas - optimising costs and climate impact - EUDP-j.nr. 64018-0512,” DGC, Hørsholm, 2020
2 | Interview with biogas Denmark (Frank Rosager), 2022, 30/10/2022
3 | Rambøll, en: Targeted efforts to reduce methane emissions from Danish biogas plants., Original title (in Danish): “Målrettet indsats for at mindske metantab fra danske biogasanlæg,” Energistyrelsen, 2021

## Hydrogen to Jet Fuel
Hydrogen to Jet Fuel
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Typical total plant size | 1,000 kt FT liquids/year | 2 | 13 | 165 | 3 | 82.5 | 247.5 | 3 | A, B, | 1, 2, 3
Typical total plant size, Output | MW | 3.1 | 20.5 | 259.6 | 4.7 | 129.8 | 389.4 | 4.7 | A, B, C | 1, 2
Input
CO2 Consumption | t/t FT Liquids | 4.3 | 3,90 | 3,30 | 4.7 | 3.3 | 3.6 | 4.7 | C, D, E
Hydrogen Consumption | MWh/MWh total input | 100% | 100% | 100% | 1.2 | 0.7 | 1.2 | 1.2 | E
Power Consumption | MWh/MWh total input | 0.5% | 0.5% | 0.5% | 0 | 0 | 0 | 0 | E
Output
FT Liquids Output | MWh/MWh total input | 0.65 | 0.7 | 0.75 | 0.8 | 0.6 | 0.9 | 0.8 | F, G, O | 1, 2
Forced outage | % | 0 | 0 | 0 |  |  |  |  | I
Planned outage | weeks per year | 3 | [7 empty] | 1
Technical lifetime | years | 25
Construction time | years | 2
Economic data
Specific investment | MUSD/MW liquids/year | 2.88 | 2.19 | 1.23 | 4.3 | 0.9 | 1.5 | 4.3 | G, J | 1, 2, 4, 5
- equipment | % | 75% | 75% | 75% |  |  |  |  | K
- installation | % | 25% | 25% | 25%
Fixed O&M | USD/MWh liquids | 23.14 | 17.39 | 10.13 | 25.5 | 9.1 | 11.1 | 25.5 | L | 1
Variable O&M | USD/MWh liquids | 7.26 | 5.75 | 2.88 | 8 | 2.6 | 3.2 | 8 | M | 4
Technology specific data
Specific investment | USD/L FT liquids/year | 4.52 | 3.42 | 1.92 | 6.8 | 1.4 | 2.4 | 6.8 | G, J | 1, 2, 4, 5
- equipment | % | 75% | 75% | 75% |  |  |  |  | K
-installation | % | 25% | 25% | 25%
Fixed O&M | USD/L FT liquids | 0.22 | 0.16 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | L | 1
Variable O&M | USD/L FT liquids | 0.07 | 0.05 | 0.03 | 0.1 | 0 | 0 | 0.1 | M | 4
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | The plant size range is based on the Schmidt and Mortensen reports and other analysis in the literature. Scale up is our assumption.
B | CO2 availability is likely to determine the maximum plant size.
C | Conversion to MW is based on 8,000 operating hours per year and the energy output in all liquid fuels. The conversion is rounded. Some reports are based on only 4,000 hours of operation.
D | Carbon efficiency in the literature ranges from 75 to 95%. Assuming that the early plants have low carbon efficiency and increase over time.
E | Denominator of FT liquids is the total liquid fuel output.
F | Hydrogen and power are the only energy input. Power will be required for pumping, compression, and utilities in addition to hydrogen production. Power estimated based on typical electric demand in petroleum refineries.
G | FT Liquids efficiency increases as hydrogen production efficiency increases with adoption of more efficient technologies. 2020 and 2030 assume alkaline electrolysis, 2040 is based on PEM systems, and 2050 assumes SOEC. Limited improvement in FT synthesis assumed, although jet fuel selectivity may improve over time.
H | Own calculations.
I | This will depend on the level of hydrogen storage and the frequency of low surplus electricity periods that are outside of the range used for the calculation of the required hydrogen storage.
J | The capital costs drop as plant size increases and through technological learning. Hydrogen storage costs are included (10% of capital costs) but not sized in the reference. No CO2 storage is assumed.
K | Own assumption.
L | Based on 5% of capital cost.
M | Based on 1.5% of capital cost. Excludes cost of power and carbon dioxide.
N | A reasonable distribution of the FT fuels might be 60% jet fuel, 20% gasoline, and 20% lighter products (LPG and fuel gas), but the distribution of outputs could be very different depending on the plant design, catalyst and the operating conditions.
References
1 | Sunfire, Sunfire Now Produces Synthetic Fuel From Air, Water And Green Electrical Energy, 2015 https://www.sunfire.de/en/company/news?file=files/sunfire/images/content/company/press/archive/2015_Apr_Sunfire%20now%20produces%20synthetic%20fuel%20from%20air.pdf
2 | NASA, NASA test: Jet biofuel may reduce climate-warming clouds, 2017. https://climate.nasa.gov/news/2601/nasa-test-jet-biofuel-may-reduce-climate-warming-clouds/
3 | Carbon Engineering. Carbon Engineering Introduction, 2019. https://ww3.arb.ca.gov/cc/scopingplan/meetings/121119/ce_cn_ccapture_dec2019.pdf
4 | Agora Verkehrswende, Agora Energiewende and Frontier Economics, The Future Cost of Electricity-Based Synthetic Fuels, 2018. https://www.agoraenergiewende.de/en/publications/the-futurecost-of-electricity-based-synthetic-fuels-1/
5 | Schmidt, P., Batteiger, V., Roth, A., Weindorf, W. and Raksha, T., Power-to-Liquids as Renewable Fuel Option for Aviation: A Review. Chemie Ingenieur Technik, 90(1-2), pp.127-140, 2018. https://doi.org/10.1002/cite.201700129