## Electricity - OH line AC
Overhead lines AC (double circuit)
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper | - | -
Energy/technical data
Energy losses, OH lines 500 kV AC at rated power | %/100 km | 1.14% | 1.14% | 1.14% | 1.14% | 1.14% | 1.14% | 0.89% | 1.39% | 0.89% | 1.39% |  | 4
Energy losses, OH lines 220 kV AC at rated power | %/100 km | 2.91% | 2.91% | 2.91% | 2.91% | 2.91% | 2.91% | 2.31% | 3.51% | 2.31% | 3.51% |  | 4
Technical life time | years | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 70 | 40 | 70 |  | 1
Typical load factor | % | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 1
Economic data
Investment, OH lines 500 kV AC, conductor size ACSR4x330 | milUSD/km | 0.91 | 0.91 | 0.89 | 0.83 | 0.77 | 0.74 | 0.66 | 1.2 | 0.51 | 0.94 | A, B, C, D, E, F | 3
Investment, OH lines 500 kV AC, conductor size ACSR4x400 | milUSD/km | 1.09 | 1.09 | 1.03 | 0.97 | 0.91 | 0.86 | 0.74 | 1.4 | 0.6 | 1.11 | A, B, C, D, E, F | 3
Investment, OH lines 500 kV AC, conductor size ACSR4x500 | milUSD/km | 1.23 | 1.23 | 1.17 | 1.11 | 1.06 | 1 | 0.86 | 1.6 | 0.69 | 1.29 | A, B, C, D, E, F | 2
Investment, OH lines 500 kV AC, conductor size ACSR4x600 | milUSD/km | 1.43 | 1.43 | 1.34 | 1.29 | 1.2 | 1.14 | 1 | 1.86 | 0.8 | 1.49 | A, B, C, D, E, F | 2
Investment, OH lines 220 kV AC, conductor size ACSR500 | milUSD/km | 0.24 | 0.24 | 0.23 | 0.22 | 0.21 | 0.19 | 0.17 | 0.32 | 0.14 | 0.25 | A, B, C, D, E, F | 3
Investment, OH lines 220 kV AC, conductor size ACSR2x330 | milUSD/km | 0.37 | 0.37 | 0.35 | 0.34 | 0.31 | 0.3 | 0.26 | 0.49 | 0.21 | 0.39 | A, B, C, D, E, F | 3
Investment, OH lines 220 kV AC, conductor size ACSR2x400 | milUSD/km | 0.47 | 0.47 | 0.45 | 0.43 | 0.4 | 0.38 | 0.33 | 0.62 | 0.27 | 0.5 | A, B, C, D, E, F | 3
Investment, OH lines 220 kV AC, conductor size ACSR3x400 | milUSD/km | 0.86 | 0.86 | 0.82 | 0.77 | 0.73 | 0.69 | 0.6 | 1.12 | 0.49 | 0.9 | A, B, C, D, E, F | 3
Investments, installation | % | 30% | 30% | 30% | 30% | 30% | 30% | - | - | - | - |  | 2, 3
Investments, materials | % | 57% | 57% | 57% | 57% | 57% | 57% | - | - | - | - |  | 2, 3
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 2, 3
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | - |  | 2, 3
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | The value is significantly lower than European sources.
B | Lower and upper uncertainties are minus/plus 30%.
C | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
D | Unit cost is corresponding to installation in weak soil conditions and routes passing through forests.
E | The investment cost of a single circuit is about 0.7 times that of a double circuit.
F | The Danish Technology Catalogue expresses investment costs in USD/km/MW. However, in Vietnam, transmission line investment costs are typically calculated in USD/km. To convert between these units, the cost in USD/km can be divided by the rated transmission capacity of the line to obtain the cost in USD/km/MW.
References
1 | I. Galiaskarov, “On reliability characteristics and service time limits of 500 kV overhead lines,” E3S Web Conf., vol. 216, p. 01014, 2020, doi: 10.1051/e3sconf/202021601014
2 | MacroPolo, “Power Play: China’s Ultra High Voltage Technology and Global Standards” [Online]. Available: https://www.paulsoninstitute.org/wp-content/uploads/2017/01/PPS_UHV_English_R.pdf
3 | EVN 2023, Unit Capital Investment for the Construction of Power Grid Projects at Voltage Levels from 110kV to 500kV.
4 | Technical parameters from catalogue of overhead conductors

## Electricity - Cable AC
Cables AC
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, cables AC at rated power | %/100 km | 1.22% | 1.22% | 1.22% | 1.22% | 1.22% | 1.22% | 0.5% | 1.93% | 0.5% | 1.93% |  | 2
Technical life time | years | 40 | 40 | 40 | 40 | 40 | 40 | 25 | 40 | 25 | 40 |  | 2
Typical load factor | % | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | [5 empty] | 2
Economic data
AC 220kV underground cables, 400 MW capacity | milUSD/km | 2.84 | 2.84 | 2.7 | 2.56 | 2.42 | 2.27 | 1.99 | 3.69 | 1.59 | 2.95 | A, B, C, E | 1, 2, 3
AC 220 kV sea cables, 400 MW capacity | milUSD/km | 6 | 6 | 5.7 | 5.4 | 5.1 | 4.8 | 4.2 | 7.8 | 3.36 | 6.24 | A, B, C, E | 1, 2, 3
AC 500kV underground cables | milUSD/km | 6.26 | 6.26 | 5.95 | 5.64 | 5.33 | 5.02 | 4.39 | 8.15 | 3.52 | 6.52 | A, B, C, D, E | 1, 2, 3, 4
AC 500kV sea cables | milUSD/km | 13.25 | 13.25 | 12.59 | 11.92 | 11.26 | 10.6 | 9.28 | 17.22 | 7.42 | 13.78 | A, B, C, D, E | 1, 2, 3, 4
Investments, installation | % | 30% | 30% | 30% | 30% | 30% | 30% | - | - | - | - |  | 1, 2
Investments, materials | % | 57% | 57% | 57% | 57% | 57% | 57% | - | - | - | - |  | 1, 2
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 1, 2
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | - |  | 1, 2
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Lower and upper uncertainties are minus/plus 30%.
B | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
C | The investment cost excludes compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
D | Based on the investment cost for the AC 220 kV underground cable, 400 MW and the ratio between investment costs for an AC 220 kV sea cable and an AC 500 kV underground cable in [4].
E | The Danish Technology Catalogue expresses investment costs in USD/km/MW. However, in Vietnam, transmission line investment costs are typically calculated in USD/km. To convert between these units, the cost in USD/km can be divided by the rated transmission capacity of the line to obtain the cost in USD/km/MW.
References
1 | X. Zhao et al., “Technical and economic demands of HVDC submarine cable technology for Global Energy Interconnection,” Glob. Energy Interconnect., vol. 3, no. 2, pp. 120–127, Apr. 2020, doi: 10.1016/j.gloei.2020.05.004
2 | Keith Bell, John Loughhead, Andrew Lovett, Katherine Jackson, and David Reid, “A comparison of electricity transmission technologies: Costs and characteristics.” [Online]. Available: https://www.theiet.org/media/axwkktkb/100110238_001-rev-j-electricity-transmission-costs-and-characteristics_final-full.pdf
3 | Investment rate of real project in Vietnam
4 | ACER, pwc, UIC, 2023

## Electricity - Substation AC
Substations AC, Onshore and Offshore
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, substation | % | 0.7% | 0.7% | 0.7% | 0.7% | 0.7% | 0.7% | 0.35% | 1.05% | 0.35% | 1.05% |  | 4, 5
Technical life time | years | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 40 | 20 | 40 |  | 4
Typical load factor | % | 60% | 60% | 60% | 60% | 60% | 60% | 50% | 70% | 50% | 70%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | - | - | - | - | A
Economic data
500 kV AC onshore substation, 600 MVA capacity, 2 bay feeders of 500 kV line, 4 bay feeders of 220 kV line | MUSD/MVA | 0.03 | 0.03 | 0.029 | 0.027 | 0.026 | 0.024 | 0.021 | 0.039 | 0.017 | 0.031 | B, C, D, E | 2
500 kV AC onshore substation, 2x600 MVA capacity, 4 bay feeders of 500 kV line, 8 bay feeders of 220 kV line | MUSD/MVA | 0.024 | 0.024 | 0.023 | 0.021 | 0.02 | 0.019 | 0.017 | 0.031 | 0.013 | 0.025 | B, C, D, E | 2
500 kV AC onshore substation, 900 MVA capacity, 2 bay feeders of 500 kV line, 6 bay feeders of 220 kV line | MUSD/MVA | 0.023 | 0.023 | 0.022 | 0.02 | 0.019 | 0.018 | 0.016 | 0.03 | 0.013 | 0.024 | B, C, D, E | 2
500 kV AC onshore substation, 2x900 MVA capacity, 4 bay feeders of 500 kV line, 8 bay feeders of 220 kV line | MUSD/MVA | 0.018 | 0.018 | 0.017 | 0.016 | 0.015 | 0.014 | 0.012 | 0.023 | 0.01 | 0.018 | B, C, D, E | 2
220 kV AC onshore substation, 125 MVA capacity, 2 bay feeders of 220 kV line, 4 bay feeders of 110 kV line | MUSD/MVA | 0.066 | 0.066 | 0.062 | 0.059 | 0.056 | 0.052 | 0.046 | 0.085 | 0.037 | 0.068 | B, C, D, E | 2
220 kV AC onshore substation, 2x125 MVA capacity, 4 bay feeders of 220 kV line, 6 bay feeders of 110 kV line | MUSD/MVA | 0.043 | 0.043 | 0.041 | 0.039 | 0.037 | 0.035 | 0.03 | 0.056 | 0.024 | 0.045 | B, C, D, E | 2
220 kV AC onshore substation, 250 MVA capacity, 4 bay feeders of 220 kV line, 6 bay feeders of 110 kV line | MUSD/MVA | 0.038 | 0.038 | 0.036 | 0.034 | 0.033 | 0.031 | 0.027 | 0.05 | 0.021 | 0.04 | B, C, D, E | 2
AC offshore substation, incl. platform, 500 MVA capacity | MUSD/MVA | 0.076 | 0.076 | 0.072 | 0.068 | 0.065 | 0.061 | 0.053 | 0.099 | 0.042 | 0.079 | B, C, D, E | 1, 3, 4
Investments, installation | % | 27% | 27% | 27% | 27% | 27% | 27% | - | - | - | - |  | 1, 4
Investments, materials | % | 60% | 60% | 60% | 60% | 60% | 60% | - | - | - | - |  | 1, 4
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 1, 4
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | -
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Project specific, depends on size and location of station.
B | Investment cost includes civil works, equipment supply and installation, testing and commissioning, project management, engineering/consultancy, and other related project costs for the defined standard substation configuration including the specified bays; it excludes land acquisition/resettlement, financing during construction, contingency, special geotechnical treatment, site grading, and VAT.
C | The investment cost excludes compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
D | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
E | Lower and upper uncertainties are minus/plus 30%.
References
1 | A. Martinez and G. Iglesias, “Multi-parameter analysis and mapping of the levelised cost of energy from floating offshore wind in the Mediterranean Sea,” Energy Convers. Manag., vol. 243, p. 114416, Sep. 2021, doi: 10.1016/j.enconman.2021.114416
2 | EVN 2023, Unit Capital Investment for the Construction of Power Grid Projects at Voltage Levels from 110kV to 500kV.
3 | T. A. Antunes, R. Castro, P. J. Santos, and A. J. Pires, “Technology Selection of High-Voltage Offshore Substations Based on Artificial Intelligence,” Energies, vol. 17, no. 17, Art. no. 17, Jan. 2024, doi: 10.3390/en17174278
4 | “Ensuring reliability: Aging substation infrastructure replacement initiative continues to make progress - Basin Electric Power Cooperative.” [Online]. Available: https://www.basinelectric.com/news-center/basin-today-stories/Ensuring-reliability-Aging-substation-infrastructure-replacement-initiative-continues-to-make-progress
5 | U.S. Department of Energy, Transmission and Distribution Components, Quadrennial Technology Review 2015

## Electricity - Transformers AC
Transformers
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, transformer | % | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0.25% | 0.17% | 0.5% | 0.17% | 0.5% |  | 4
Technical life time | years | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1, 2
Typical load factor | % | 60% | 60% | 60% | 60% | 60% | 60% | - | - | - | -
Construction time | years | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - |  | 1, 2
Economic data
500/220 kV, 900 MVA | MUSD/MVA | 0.012 | 0.012 | 0.011 | 0.01 | 0.01 | 0.009 | 0.008 | 0.015 | 0.006 | 0.012 | A, B, C | 3
500/220 kV, 600 MVA | MUSD/MVA | 0.015 | 0.015 | 0.014 | 0.013 | 0.013 | 0.012 | 0.01 | 0.019 | 0.008 | 0.015 | A, B, C | 3
500/220 kV, 450 MVA | MUSD/MVA | 0.016 | 0.016 | 0.016 | 0.015 | 0.014 | 0.013 | 0.011 | 0.021 | 0.009 | 0.017 | A, B, C | 3
220/110 kV, 250 MVA | MUSD/MVA | 0.019 | 0.019 | 0.018 | 0.017 | 0.016 | 0.015 | 0.013 | 0.025 | 0.011 | 0.02 | A, B, C | 3
220/110 kV, 125 MVA | MUSD/MVA | 0.026 | 0.026 | 0.024 | 0.023 | 0.022 | 0.02 | 0.018 | 0.033 | 0.014 | 0.027 | A, B, C | 3
Investments, installation | % | 27% | 27% | 27% | 27% | 27% | 27% | - | - | - | - |  | 3
Investments, materials | % | 60% | 60% | 60% | 60% | 60% | 60% | - | - | - | - |  | 3
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 3
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | -
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Lower and upper uncertainty are minus/plus 30%.
B | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
C | The investment cost excludes compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
References
1 | L. W. McGrail T., “Transformer life expectancy: How long will your transformers last?” [Online]. Available: https://h2scan.com/wp-content/uploads/2025/05/h2scan-nov2024-transformersmag-articlereprint-v2.pdf
2 | R. Marketing, “Understanding Transformer Aging and Life Expectancy,” A Line EDS [Online]. Available: https://www.alineeds.com/understanding-transformer-aging-and-life-expectancy/
3 | EVN 2023, Unit Capital Investment for the Construction of Power Grid Projects at Voltage Levels from 110kV to 500kV.
4 | Technical Parameters from catalogue of transformers

## Electricity - Compensation
Compensation
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Technical life time | years | 40 | 40 | 40 | 40 | 40 | 40
Typical load factor | % | 60% | 60% | 60% | 60% | 60% | 60% | [5 empty] | 1
Construction time | years | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [5 empty] | 1
Economic data
Capacitor bank | MUSD/MVAr | 0.034 | 0.034 | 0.0323 | 0.0306 | 0.0289 | 0.027 | 0.024 | 0.044 | 0.019 | 0.035 | A, B | 1
SVC | MUSD/MVAr | 0.086 | 0.086 | 0.0817 | 0.0774 | 0.0731 | 0.069 | 0.06 | 0.112 | 0.048 | 0.089 | A, B | 1
Reactor | MUSD/MVAr | 0.036 | 0.036 | 0.0342 | 0.0324 | 0.0306 | 0.029 | 0.025 | 0.047 | 0.02 | 0.037 | A, B | 1
STATCOM | MUSD/MVAr | 0.222 | 0.222 | 0.2109 | 0.1998 | 0.1887 | 0.18 | 0.155 | 0.289 | 0.124 | 0.231 | A, B | 1
Investments, installation | % | 27% | 27% | 27% | 27% | 27% | 27% | - | - | - | -
Investments, materials | % | 60% | 60% | 60% | 60% | 60% | 60% | - | - | - | -
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | -
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | - |  | 1
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Lower and upper uncertainty are minus/plus 30%.
B | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
References:
1 | Danish Energy Agency, 2025 - Technology Data for Energy Transport

## Electricity - OH line DC
Overhead lines DC (double circuit)
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, OH lines DC at rated power | %/100 km | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.1% | 0.5% | 0.1% | 0.5% |  | 2, 3, 5
Technical life time | years | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 70 |  | 1
Typical load factor | % | 80% | 80% | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 3 |  | 1
Economic data
Investment, OH lines 500 kV DC | milUSD/km | 1.14 | 1.14 | 1.07 | 1.03 | 0.96 | 0.91 | 0.8 | 1.49 | 0.64 | 1.19 | A, B, C, D, E, G | 4, 6, 7
Investment, OH lines 800 kV DC | milUSD/km | 1.83 | 1.83 | 1.72 | 1.65 | 1.54 | 1.46 | 1.28 | 2.38 | 1.02 | 1.9 | A, B, C, D, E, F, G | 4, 6, 7
Investments, installation | % | 30% | 30% | 30% | 30% | 30% | 30% | - | - | - | - |  | 2, 4
Investments, materials | % | 57% | 57% | 57% | 57% | 57% | 57% | - | - | - | - |  | 2, 4
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 2, 4
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | - |  | 2, 4
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Based on the investment cost estimate for OH line 500 kV AC, conductor size ACSR4x600 (double circuit) in cost per km. and applying a DC to AC cost ratio of 80 % (MEUR/km) taken from [7], where they estimate comparable AC OH lines to cost 2.50 MEUR/km and DC OH lines to cost 2.00 MEUR/km (= 80 %).
B | The investment cost represents line-only overhead transmission costs and excludes HVDC terminal/converter, compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
C | Unit cost is corresponding to installation in weak soil conditions and routes passing through forests.
D | Lower and upper uncertainties are minus/plus 30%.
E | Prices are assumed to decrease linearly from 2030 to 2050 with 20%.
F | Based on the 500 kV DC line-only estimate using an engineering uplift of 1.6 (1.4 - 1.8) on cost per km to reflect the heavier line class of 800 kV overhead lines. This uplift is informed by voltage-class design differences from [8] and should be treated as an assumption.
G | The Danish Technology Catalogue expresses investment costs in USD/km/MW. However, in Vietnam, transmission line investment costs are typically calculated in USD/km. To convert between these units, the cost in USD/km can be divided by the rated transmission capacity of the line to obtain the cost in USD/km/MW.
References
1 | I. Galiaskarov, “On reliability characteristics and service time limits of 500 kV overhead lines,” E3S Web Conf., vol. 216, p. 01014, 2020, doi: 10.1051/e3sconf/202021601014
2 | MacroPolo, “Power Play: China’s Ultra High Voltage Technology and Global Standards”. [Online]. Available: https://www.paulsoninstitute.org/wp-content/uploads/2017/01/PPS_UHV_English_R.pdf
3 | W. F. Pickard, “The limits of HVDC transmission,” Energy Policy, vol. 61, pp. 292–300, Oct. 2013, doi: 10.1016/j.enpol.2013.03.030
4 | EVN 2023, Unit Capital Investment for the Construction of Power Grid Projects at Voltage Levels from 110kV to 500kV
5 | Technical parameters from catalogue of overhead conductors
6 | Netzentwicklungsplan Strom (German TSOs), version 2021
7 | MISO 2024, Transmission Cost Estimation Guide for MTEP24

## Electricity - Cable DC
Cables DC
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, cables DC at rated power | %/100 km | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.1% | 1% | 0.1% | 1% |  | 1
Technical life time | years | 40 | 40 | 40 | 40 | 40 | 40 | 25 | 40 | 25 | 40 |  | 2
Typical load factor | % | 80% | 80% | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | - | - | - | - |  | 2
Economic data
DC underground cables, 1500-2000 MW capacity | milUSD/km | 16.6 | 16.6 | 15.78 | 14.94 | 14.12 | 13.28 | 11.62 | 21.58 | 9.3 | 17.26 | A, B, C, D | 2, 3
DC sea cables, 1500-2000 MW capacity | milUSD/km | 34.6 | 34.6 | 32.88 | 31.14 | 29.42 | 27.68 | 24.22 | 44.98 | 19.38 | 35.98 | A, B, C, D | 2, 3
Investments, installation | % | 30% | 30% | 30% | 30% | 30% | 30% | - | - | - | - |  | 2, 3
Investments, materials | % | 57% | 57% | 57% | 57% | 57% | 57% | - | - | - | - |  | 2, 3
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 2, 3
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | - |  | 2, 3
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | The investment cost excludes compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
B | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
C | Lower and upper uncertainties are minus/plus 30%.
D | The Danish Technology Catalogue expresses investment costs in USD/km/MW. However, in Vietnam, transmission line investment costs are typically calculated in USD/km. To convert between these units, the cost in USD/km can be divided by the rated transmission capacity of the line to obtain the cost in USD/km/MW.
References
1 | Institute for Energy and Transport (Joint Research Centre), M. Ardelean, and P. Minnebo, HVDC submarine power cables in the world: state of the art knowledge. Publications Office of the European Union, 2015. [Online]. Available: https://data.europa.eu/doi/10.2790/023689
2 | X. Zhao et al., “Technical and economic demands of HVDC submarine cable technology for Global Energy Interconnection,” Glob. Energy Interconnect., vol. 3, no. 2, pp. 120–127, Apr. 2020, doi: 10.1016/j.gloei.2020.05.004
3 | Keith Bell, John Loughhead, Andrew Lovett, Katherine Jackson, and David Reid, “A comparison of electricity transmission technologies: Costs and characteristics.” [Online]. Available: https://www.theiet.org/media/axwkktkb/100110238_001-rev-j-electricity-transmission-costs-and-characteristics_final-full.pdf

## Electricity - Substation DC
Substations DC, Onshore and Offshore
Parameter | Unit | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[8 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, DC LCC substation | % | 0.8% | 0.8% | 0.8% | 0.8% | 0.8% | 0.8% | 0.7% | 1.6% | 0.7% | 1.6% |  | 4, 5
Energy losses, DC VSC substation | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2% | 1% | 2% |  | 4, 5
Technical life time | years | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 40 | 20 | 40 |  | 2
Typical load factor | % | 80% | 80% | 80% | 80% | 80% | 80% | 70% | 90% | 70% | 90%
Construction time | years | 2 | 2 | 2 | 2 | 2 | 2 | - | - | - | - | A
Economic data
DC LCC onshore substation, 1000-1250 MW capacity | MUSD/MW | 0.11 | 0.11 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08 | 0.14 | 0.06 | 0.11 | B, C, D, E | 3
DC VSC onshore substation, 1000-1250 MW capacity | MUSD/MW | 0.17 | 0.17 | 0.16 | 0.15 | 0.14 | 0.14 | 0.12 | 0.22 | 0.1 | 0.18 | B, C, D, E | 3
DC offshore substation, incl. platform, 1500-2000 MW capacity | MUSD/MW | 0.45 | 0.45 | 0.42 | 0.4 | 0.38 | 0.36 | 0.31 | 0.58 | 0.25 | 0.46 | B, C, D, E | 1, 2
Investments, installation | % | 27% | 27% | 27% | 27% | 27% | 27% | - | - | - | - |  | 1, 2
Investments, materials | % | 60% | 60% | 60% | 60% | 60% | 60% | - | - | - | - |  | 1, 2
Additional costs | % | 13% | 13% | 13% | 13% | 13% | 13% | - | - | - | - |  | 1, 2
Fixed O&M | % of CAPEX/year | 2% | 2% | 2% | 2% | 2% | 2% | - | - | - | -
Variable O&M | USD/MWh/km | - | - | - | - | - | - | - | - | - | -
Notes:
A | Project specific, depends on size and location of station.
B | Estimates, project specific, depends on size and location of station. DC substation includes converter, converter transformers, AC switchgear and busbars, harmonic filters, lightning towers, ancillary plant etc.
C | The investment cost excludes compensation, support and resettlement costs, interest during construction, initial working capital, contingency costs, and VAT.
D | Prices assumed to decrease linearly from 2030 to 2050 with 20%.
E | Lower and upper uncertainties are minus/plus 30%.
References
1 | A. Martinez and G. Iglesias, “Multi-parameter analysis and mapping of the levelised cost of energy from floating offshore wind in the Mediterranean Sea,” Energy Convers. Manag., vol. 243, p. 114416, Sep. 2021, doi: 10.1016/j.enconman.2021.114416.
2 | “Ensuring reliability: Aging substation infrastructure replacement initiative continues to make progress - Basin Electric Power Cooperative.” [Online]. Available: https://www.basinelectric.com/news-center/basin-today-stories/Ensuring-reliability-Aging-substation-infrastructure-replacement-initiative-continues-to-make-progress
3 | IE&DEA, Analysis of HVDC for PDP8 Vietnam, 2020
4 | National grid, "High voltage direct current electricity - technical information"
5 | Xin Fang, "HVDC for offshore wind", 2025

## H2 pipeline - 70 bar
Transport of H2 by pipeline - 70 bar
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper | - | -
Energy/technical data
Energy losses, pipelines 1-100 MW | %/1000 km | 9.7% | 9.3% | 8.3% | 7.9% | 16% | 7.3% | 13.6% | A | 1
Energy losses, pipelines 100-250 MW | %/1000 km | 7.9% | 7.6% | 6.8% | 6.4% | 13.1% | 6% | 11.2% | A | 1
Energy losses, pipelines 250-500 MW | %/1000 km | 6.1% | 5.8% | 5.2% | 4.9% | 10.1% | 4.6% | 8.6% | A | 1
Energy losses, pipelines 500-1500 MW | %/1000 km | 4.3% | 4.1% | 3.7% | 3.4% | 7.1% | 3.2% | 6.1% | A | 1
Energy losses, pipelines 1500-5000 MW | %/1000 km | 2.8% | 2.7% | 2.4% | 2.3% | 4.7% | 2.1% | 4% | A | 1
Energy losses, pipelines 5000-20000 MW | %/1000 km | 2.1% | 2% | 1.8% | 1.7% | 3.5% | 1.6% | 3% | A | 1
Energy losses, pipelines above 20000 MW | %/1000 km | 1.6% | 1.5% | 1.3% | 1.3% | 2.6% | 1.1% | 2.1% | A | 1
Energy demand, compressor filling station | % | 0.9% | 0.8% | 0.7% | 0.7% | 3% | 0.6% | 2.1% | B | 1
Technical life time | years | 50 | 50 | 50 | 45 | 55 | 45 | 55 |  | 1
Construction time | years | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1
Economic data
Investment costs; 0-100 MW | USD/MW/m | 5.3 | 5.2 | 4.9 | 4.9 | 6.9 | 4.5 | 6.3 | C, F | 1
Investment costs; 100-250 MW | USD/MW/m | 2.4 | 2.3 | 2.2 | 2.2 | 3 | 2 | 2.7 | C, F | 1
Investment costs; 250-500 MW | USD/MW/m | 1.4 | 1.4 | 1.4 | 1.4 | 1.9 | 1.3 | 1.7 | C, F | 1
Investment costs; 500-1000 MW | USD/MW/m | 1 | 1 | 1 | 1 | 1.3 | 0.9 | 1.2 | C, F | 1
Investment costs; 1000-4000 MW | USD/MW/m | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | C, F | 1
Investment costs; above 6000 MW | USD/MW/m | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | C, F | 1
Investments, installation | % | 77.5% | 77.5% | 77.5% | 75% | 80% | 70% | 80% | D | 1
Investments, materials | % | 22.5% | 22.5% | 22.5% | 20% | 25% | 20% | 30% | D | 1
Fixed O&M | USD/km/year/MW | 0.5 | 0.36 | 0.3 | 0.3 | 1.4 | 0.2 | 1.4 | E | 1
Variable O&M | USD/MW/km | - | - | - | - | - | - | - |  | 1
Notes:
A | Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. Currently, the optimum seems to be: Velocity (m/s) ≈ 4.4*Q0.1, dPdL(bar/km) ≈ 1.28*Q-0.75, Q = energy flow (MW).
B | Energy to compress from 35 barg to 140 barg. This value can be lowered by only compressing to current operation pressure in transmission line using outtake from interstage compressors.
C | Estimate includes: Installation based on buried pipeline with 8% tunneling, coating, sectionalization with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting and landowner compensation.
D | Installation cost is ~80% for small pipes and ~75% for large pipes.
E | Fixed operation cost is per pipe length and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
F | This parameter refers to single-line pipelines.
References
1 | Danish Energy Agency, 2025 - Technology Data for Energy Transport

## H2 pipeline - 140 bar
Transport of H2 by pipeline - 140 bar
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses, pipelines 1-100 MW | %/1000 km | 7.5% | 7% | 6.3% | 6% | 12.1% | 5.5% | 10.3% | A | 1
Energy losses, pipelines 100-250 MW | %/1000 km | 6.4% | 5.9% | 5.3% | 5% | 10.2% | 4.6% | 8.7% | A | 1
Energy losses, pipelines 250-500 MW | %/1000 km | 5.1% | 4.7% | 4.2% | 3.9% | 8.1% | 3.7% | 6.9% | A | 1
Energy losses, pipelines 500-1500 MW | %/1000 km | 3.8% | 3.5% | 3.1% | 3% | 6.1% | 2.7% | 5.2% | A | 1
Energy losses, pipelines 1500-5000 MW | %/1000 km | 2.7% | 2.5% | 2.2% | 2.1% | 4.2% | 1.9% | 3.6% | A | 1
Energy losses, pipelines 5000-20000 MW | %/1000 km | 2.1% | 1.9% | 1.7% | 1.6% | 3.3% | 1.5% | 2.8% | A | 1
Energy losses, pipelines above 20000 MW | %/1000 km | 1.5% | 1.4% | 1.3% | 1.3% | 2.5% | 1.1% | 2.1% | A | 1
Energy demand, compressor filling station | % | 2.1% | 1.7% | 1.5% | 1.3% | 3.5% | 0.9% | 2.5% | B | 1
Technical life time | years | 50 | 50 | 50 | 45 | 55 | 45 | 55 |  | 1
Construction time | years | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1
Economic data
Investment costs; 0-100 MW | USD/MW/m | 5.8 | 5.6 | 5.3 | 5.3 | 7.5 | 4.8 | 6.8 | C, F | 1
Investment costs; 100-250 MW | USD/MW/m | 2.5 | 2.4 | 2.3 | 2.3 | 3.3 | 2.2 | 3 | C, F | 1
Investment costs; 250-500 MW | USD/MW/m | 1.6 | 1.6 | 1.4 | 1.4 | 2 | 1.3 | 1.9 | C, F | 1
Investment costs; 500-1000 MW | USD/MW/m | 1.1 | 1 | 1 | 1 | 1.3 | 0.9 | 1.3 | C, F | 1
Investment costs; 1000-4000 MW | USD/MW/m | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.7 | C, F | 1
Investment costs; above 6000 MW | USD/MW/m | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | C, F | 1
Investments, percentage installation | % | 77.5% | 77.5% | 77.5% | 75% | 80% | 70% | 80% | D | 1
Investments, percentage materials | % | 22.5% | 22.5% | 22.5% | 20% | 25% | 20% | 30% | D | 1
Fixed O&M | USD/km/year/MW | 0.5 | 0.36 | 0.3 | 0.3 | 1.4 | 0.2 | 1.4 | E | 1
Variable O&M | USD/MW/km | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1
Notes:
A | Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. Currently, the optimum seems to be: Velocity (m/s) ≈ 4.4*Q0.1, dPdL(bar/km) ≈ 1.28*Q-0.75, Q = energy flow (MW).
B | Energy to compress from 35 barg to 140 barg. This value can be lowered by only compressing to current operation pressure in transmission line using outtake from interstage compressors.
C | Estimate includes: Installation based on buried pipeline with 8% tunneling, coating, sectionalization with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting and landowner compensation.
D | Installation cost is ~80% for small pipes and ~75% for large pipes.
E | Fixed operation cost is per pipe length and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
F | This parameter refers to single-line pipelines.
References
1 | Danish Energy Agency, 2025 - Technology Data for Energy Transport

## NH3 - Pipeline
Transport of NH3 by pipeline
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Energy losses | ‰ | <0.1‰ | <0.1‰ | <0.1‰ | 0.01‰ | 0.1‰ | 0.01‰ | 0.1‰ | A, B | 1
Technical life time | years | 50 | 50 | 50 | 45 | 55 | 45 | 55 |  | 1
Construction time | years | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1
Economic data
Investment costs; 1-15 MW | USD/MW/m | 14.6 | 13.8 | 13.3 | 13.08 | 21.8 | 11.94 | 18.57 | B, C, F | 1
Investment costs; 15-30 MW | USD/MW/m | 9.7 | 9.2 | 8.8 | 8.69 | 14.48 | 7.93 | 12.34 | B, C, F | 1
Investment costs; 30-100 MW | USD/MW/m | 4 | 3.9 | 3.6 | 3.61 | 6.01 | 3.29 | 5.13 | B, C, F | 1
Investment costs; 100-300 MW | USD/MW/m | 1.9 | 1.7 | 1.7 | 1.65 | 2.74 | 1.5 | 2.34 | B, C, F | 1
Investment costs; 300-500 MW | USD/MW/m | 1 | 1 | 1 | 0.95 | 1.58 | 0.86 | 1.34 | B, C, F | 1
Investment costs; 500-1000 MW | USD/MW/m | 0.6 | 0.6 | 0.6 | 0.57 | 0.95 | 0.52 | 0.81 | B, C, F | 1
Investment costs; 1000-2000 MW | USD/MW/m | 0.4 | 0.3 | 0.3 | 0.33 | 0.55 | 0.3 | 0.47 | B, C, F | 1
Investment costs; above 2000 MW | USD/MW/m | 0.3 | 0.3 | 0.3 | 0.26 | 0.43 | 0.24 | 0.37 | B, C, F | 1
Investments, installation | % | 87% | 82.7% | 78.3% | 80% | 90% | 75% | 90% | D | 1
Investments, materials | % | 13% | 17.4% | 21.7% | 10% | 20% | 10% | 25% | C | 1
Fixed O&M | USD/km/year/MW | 144 | 144 | 144 | 72 | 288 | 72 | 288 | E | 1
Variable O&M | USD/MW/km | - | - | - | - | - | - | - |  | 1
Notes:
A | Energy required to overcome pipeline pressure drop (dP). Optimal dP/km depend on cost of booster compressor vs pipe material cost. Currently, the optimum seems to be: Velocity (m/s) ≈ 4.4*Q0.1, dPdL(bar/km) ≈ 1.28*Q-0.75, Q = energy flow (MW).
B | Energy to compress from 35 barg to 140 barg. This value can be lowered by only compressing to current operation pressure in transmission line using outtake from interstage compressors.
C | Estimate includes: Installation based on buried pipeline with 8% tunneling, coating, sectionalization with depressurizations vents for every 20 km, cathodic protection, coating, pressure boosting stations, permitting and landowner compensation.
D | Installation cost is ~80% for small pipes and ~75% for large pipes.
E | Fixed operation cost is per pipe length and capacity. 4% of CAPEX is assumed in 2020, 2% in 2030 and 1.5% in 2050.
F | This parameter refers to single-line pipelines.
References
1 | Danish Energy Agency, 2025 - Technology Data for Energy Transport

## Natural gas - Pipeline
Transport of natural gas by pipeline
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Economic data
NG: Investment cost | USD/tonNG | 1.04 | 0.94 | 0.63 | 0.8 | 1.04 | 0.34 | 0.94 | A, C, D | 1, 2, 3, 4, 5, 6
NG: Fixed O&M cost | USD/tonNG/y | 0.24 | 0.23 | 0.19 | 0.21 | 0.24 | 0.12 | 0.23 | B, C, D | 1, 2, 3, 4, 5, 6
Notes:
A | Pipeline tariff is about 0.025 USD/tr.BTU based on Vietnamese LNG pipeline assessments.
B | Fixed O&M assumption is 5.72% of construction and equipment cost. Construction and equipment cost is about 70% of CAPEX.
C | Tariff decomposition into investment (0.020 USD/tr.BTU) and fixed O&M (0.0046 USD/tr.BTU).
D | LNG heating value: 1 ton is 52 million BTU.
References
1 | Report on gas supply plan for Nhon Trach Power Center
2 | AFRY, https://afry.com/en/area/energy, 2021
3 | GIIGNL, LNG Industry Annual Report, 2023
4 | U.S. EIA, Natural Gas Explained: Conversion Factors, 2022
5 | Vietnamese LNG Pipeline Investment Studies, 2020–2023
6 | Internal Engineering & Financial Assessments for LNG Supply to Power Plants, 2023–2024

## LH2, L20, LHC - Ship
Transport of LH2, L20 and LHC by ship
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper | - | -
Energy/technical data
LH2: Energy demand | MJ/km | 1487 | 1413 | 1115 | - | - | - | - | A, J
L20: Energy demand | MJ/km | 2500 | 2375 | 1875 | - | - | - | - | A, J
LHC: Energy demand | MJ/km | 3300 | 3135 | 2475 | - | - | - | - | A, J
Technical life time | year | 20 | 20 | 20 | - | - | - | - | B
Economic data
LH2: Investment cost | USD/tonH2 | 37455 | 44484 | 97470 | 43420 | 46675 | 80344 | 107283 | C, D, E, F | 1
L20: Investment cost | USD/tonL20 | 1923 | 2284 | 5005 | 1923 | 2397 | 4125 | 5508 | C, D, E, F | 1
LHC: Investment cost | USD/tonLHC | 6909 | 8206 | 17980 | 6909 | 8610 | 14821 | 19790 | C, D, E, F | 1
LH2: Fixed O&M cost | USD/tonH2/year | - | - | - | - | - | - | -
L20: Fixed O&M cost | USD/tonL20/year | - | - | - | - | - | - | -
LHC: Fixed O&M cost | USD/tonLHC/year | - | - | - | - | - | - | -
LH2: Port cost | USD/tonH2 | 4966 | 4723 | 3863 | 4264 | 4966 | 2568 | 4723 | G, H, I | 1
L20: Port cost | USD/tonL20 | 106 | 101 | 82 | 91 | 106 | 55 | 101 | G, H, I | 1
LHC: Port cost | USD/tonLHC | 356 | 339 | 277 | 306 | 356 | 184 | 339 | G, H, I | 1
Notes:
A | Energy demand values reflect baseline propulsion energy requirements for LH₂, L20, and LHC vessels, including relevant fuel-loss characteristics.
B | A technical lifetime of 20 years is applied consistently for all shipping assets in the transport modelling assumptions.
C | Investment cost calculated for ship capacity: (i) LH2: 11000 tons; (ii) L20: 26000 tons; (iii) LHC: 11000 tons.
D | Base-year investment costs remain constant in the source dataset, with any future reductions applied externally for scenario modelling.
E | LH₂ ship CAPEX represents total vessel construction cost including cryogenic containment, insulation and safety systems. L20 and LHC ship CAPEX reflects representative tanker sizes and associated cargo-handling system costs.
F | Investment cost scenarios reflect stable costs under conservative conditions, moderate reductions from design and procurement optimization, and aggressive reductions linked to technological advances and shipbuilding economies of scale.
G | Port cost values represent export-side storage and handling infrastructure requirements for LH₂, L20, and LHC.
H | Port operations assume typical berthing conditions, ancillary services, and handling activities required for hydrogen carriers.
I | Port cost scenarios maintain constant fees conservatively, with moderate efficiency-driven reductions, and aggressive declines from digitalization, operational streamlining, and standardized hydrogen-handling procedures.
J | It is assumed that the efficiency of the combustion engine is improved so it is 95% in 2030 of the efficiency in 2025 and 75% in 2050. The 75% is based on the difference between the efficiency of a traditional combustion engine and a fuel cell engine. The 95% is based on natural replacement of old tankers with new tankers that have a more efficient engine (some of them might be fuel cells) and revamp of existing engines.
References
1 | GIZ, “Recommended Medium to Long-Term Strategy of Oil & Gas and Chemical Industries in Vietnam”

## LNG - Ship
Transport of LNG by ship
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
LNG: Energy demand | ton/day | 108 | 190 | 1836 |  |  |  |  | B | 1
Technical life time | year | 20 | 20 | 20
Economic data
LNG: Investment cost | USD/tonLNG | 537 | 461 | 251 | 394 | 537 | 134 | 461 | A, B, G | 1
LNG: Fixed O&M cost | USD/ton/y | - | - | - | - | - | - | - | C
LNG: Port fee | USD/tonLNG | 10.4 | 9.4 | 6.28 | 10.4 | 8.05 | 9.4 | 2.73 | D, G | 1
LNG: Port cost | USD/tonLNG | 3.6 | 3.42 | 2.8 | 3.6 | 3.09 | 3.42 | 0.99 | D, G | 1
LNG: Shipping cost | USD/tonLNG | 22.9 | 20.7 | 13.8 | 22.9 | 18.7 | 20.7 | 6 | E, F, G | 1

## Coal - Conveyor
Transport of coal (domestic) by conveyor
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper | - | -
Economic data
Transfer station handling cost | USD/ton | 0.13 | 0.13 | 0.11 | 0.12 | 0.13 | 0.04 | 0.13 | A, B, C, D, E, F, G, H, I, J, K | 1
Conveying cost | USD/ton-km | 4.3 | 4.19 | 3.79 | 4.09 | 4.3 | 1.22 | 4.19 | A, B, C, D, E, F, G, H, I, J, K | 1
Notes:
A | Conveyor operating cost is sensitive to electricity tariffs.
B | Belt, roller and mechanical wear determine maintenance frequency and cost.
C | Transfer-station handling costs depend on site layout and throughput.
D | Labour requirements for inspection, lubrication and monitoring vary with system size and utilisation.
E | Terrain profile, elevation change and conveying distance impact efficiency.
F | Long-term projections must consider electricity-tariff variability and materials cost.
G | Improved materials, automation and monitoring systems may gradually reduce O&M cost.
H | Industrial safety and compliance requirements may introduce additional operational expenses.
I | Cost parameters are based on domestic datasets for conveyor-based coal-handling systems used at mines, industrial yards and power-plant receiving stations.
J | Electricity cost assumptions follow MOIT tariff decisions, which directly affect conveyor operating cost.
K | Scenario factors reflect equipment durability, automation levels and O&M practices of conveyor systems in Viet Nam.
References
1 | Ministry of Industry and Trade of Vietnam (2025). Decision No. 1279/QD-BCT dated May 9, 2025, on the promulgation of the average retail electricity price.

## Coal - Ship
Transport of coal (domestic) by ship
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Economic data
Port fee | USD/ton | 2.79 | 2.52 | 1.68 | 2.16 | 2.79 | 0.73 | 2.52 | A, B, C, D, E, F, G, H, I, J, K | 1, 2
Shipping cost | USD/ton | 1.38 | 1.25 | 0.83 | 1.13 | 1.38 | 0.36 | 1.25 | A, B, C, D, E, F, G, H, I, J, K | 1, 2
Notes:
A | Costs are sensitive to marine fuel prices and freight-market fluctuations.
B | Port-service tariffs (pilotage, tug assistance, berthing) vary by terminal and influence total cost.
C | Vessel chartering rates depend on fleet availability and seasonal utilisation.
D | Maintenance, labour and insurance costs evolve with regulatory and market conditions.
E | Weather, navigation depth and routing constraints affect voyage efficiency.
F | Long-term projections must account for uncertainty in shipping fuel prices and port-fee adjustments.
G | Cost reductions may arise from improved scheduling, fleet optimisation and engine-efficiency upgrades.
H | Maritime environmental or safety requirements may introduce additional compliance costs.
I | USD/ton values represent aggregated maritime transport costs for representative coastal shipping routes, implicitly reflecting distance-based cost components.
J | Based on cost from Russian to Viet Nam.
K | Scenario factors reflect observed variations in port charges, vessel-fleet utilisation and coastal freight-market conditions relevant to northern Viet Nam.
References
1 | Cost parameters for port fees and coastal shipping derived from domestic coal-transport datasets covering operations on the Quang Ninh–Hai Phong route
2 | Supplementary information from operational data of Hai Phong thermal power plants and market sources on vessel chartering, port-service tariffs and marine fuel consumption

## Coal - Truck
Transport of coal (domestic) by truck
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper | - | -
Economic data
Yard / terminal handling fee | USD/ton | 0.32 | 0.3 | 0.25 | 0.27 | 0.32 | 0.09 | 0.3 | A, B, C, D, E, F, G, H, I, J, K | 1
Yard / terminal fixed cost | USD | 2 | 1.9 | 1.56 | 1.81 | 2 | 0.55 | 1.9 | A, B, C, D, E, F, G, H, I, J, K | 1
Trucking cost | USD/ton-km | 0.058 | 0.055 | 0.045 | 0.053 | 0.058 | 0.016 | 0.055 | A, B, C, D, E, F, G, H, I, J, K | 1
Notes:
A | Trucking cost is highly sensitive to diesel prices and vehicle fuel consumption.
B | Road conditions, congestion and distance characteristics directly influence travel time and cost.
C | Handling and unloading fees vary by receiving point and operation type.
D | Labour, maintenance, tyre wear and spare-parts prices contribute to cost variability.
E | Fleet age, availability and load-factor utilisation affect cost efficiency.
F | Long-term projections must consider fuel-price uncertainty and road-regulation changes.
G | Route optimisation, fleet renewal and driver training may yield gradual cost reductions.
H | Environmental and safety compliance requirements may increase operating cost.
I | Cost parameters are derived from domestic datasets on short-distance coal trucking to industrial facilities and thermal power plants.
J | Market data include diesel prices, labour and maintenance costs, and typical handling fees at receiving sites.
K | Scenario factors reflect fleet utilisation, road conditions and standard domestic trucking practices.
References
1 | PVOIL, Gasoline price list, https://www.pvoil.com.vn/tin-gia-xang-dau

## Coal - Train
Transport of coal (domestic) by train
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Economic data
Rail transport cost | USD/ton | 30 | 27.12 | 18.1 | 23.21 | 30 | 7.87 | 27.12 | A, B, C, D, E, F, G, H, I, J, K, L | 1
Notes:
A | Rail-transport cost is influenced by diesel prices and locomotive efficiency.
B | Tariffs depend on wagon availability, network congestion and operator pricing policies.
C | Rail terminal and yard-handling fees vary by location and service level.
D | Labour, maintenance and rolling-stock refurbishment costs follow market and inflation trends.
E | Track condition, gradients and routing constraints affect travel time and operating efficiency.
F | Long-term projections must reflect uncertainty in fuel markets and tariff adjustments.
G | Efficiency gains may come from wagon standardisation, improved scheduling and locomotive upgrades.
H | Safety or signaling-system requirements can influence long-term cost structures.
I | USD/ton values represent aggregated rail transport costs for representative inland routes, implicitly reflecting distance-based cost components.
J | Cost assumptions are based on domestic rail-freight datasets for bulk coal movement within Viet Nam.
K | Tariff structures are obtained from Vietnam Railways and relevant logistics operators.
L | Scenario factors reflect locomotive efficiency, wagon availability and typical pricing mechanisms in Vietnamese rail freight.
References:
1 | Vietnam Post Logistics, [Update] Latest Rail Freight Rates 2025: Detailed Price List & Standard Calculation Method for Businesses, https://vietnampostlogistics.com/gia-cuoc-duong-sat-2025