## Supercritical coal power plant
Supercritical coal power plant
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 300 | 1800 | 300 | 1800 |  | 1
Electrical efficiency, net, name plate | % | 37.7 | 38.8 | 39.4 | 39.9 | 33 | 40 | 35 | 42 |  | 1, 5, 6
Electrical efficiency, net, annual average | % | 36.7 | 37.8 | 38.3 | 38.9 | 33 | 40 | 35 | 42 |  | 1, 6
Forced outage | % | 7 | 6 | 5 | 3 | 5 | 15 | 2 | 7 | A | 1
Planned outage | % | 13.5 | 9.6 | 7.7 | 5.8 | 5.8 | 15.4 | 3.8 | 7.7 | A | 1
Self-consumption | % | 6 | 6 | 6 | 6 | 5 | 8 | 5 | 8
Technical lifetime | years | 30 | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Construction time | years | 3.75 | 3 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
Space requirement | 1000_m2/MW_e | 1.85 | 1.85 | 1.85 | 1.85 | 1 | 2.75 | 1 | 2.75 |  | 6
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 2 | 4 | 4 | 4 | 1 | 4 | 3 | 4 | B | 1
Minimum load | % of full load | 50 | 25 | 22.5 | 20 | 25 | 75 | 10 | 30 | A | 1
Warm start-up time | hours | 6 | 4 | 4 | 4 | 2 | 8.5 | 2 | 5 | B | 1
Cold start-up time | hours | 10 | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Minimum Up time | hours | 6 | 6 | 6 | 6 | - | - | - | - |  | 7
Minimum Down time | hours | 4 | 4 | 4 | 4 | - | - | - | - |  | 7
Environment
PM 2.5 | mg/Nm3 | 70 | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2, 3
SO2 (degree of desulphuring) | % | 86 | 86 | 86 | 95 | 73 | 95 | 73 | 95 |  | 2, 3
NOX | g/GJ_i | 115 | 113 | 76 | 38 | 115 | 263 | 38 | 263 | C | 2, 3
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 1.81 | 1.79 | 1.75 | 1.72 | 1.35 | 2.44 | 1.29 | 2.15 | D, F, G, H | 1, 5, 6
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M | USD/MW_e/year | 49301 | 48810 | 47843 | 46895 | 36976 | 66557 | 35171 | 58618 | F, H | 1, 5, 6
Variable O&M | USD/MWh | 1.4 | 1.4 | 1.39 | 1.36 | 1.05 | 1.89 | 1.02 | 1.7 | F, H | 1, 6
Start-up costs | USD/MW_e/start-up | 125 | 65 | 65 | 65 | 94 | 169 | 49 | 81 | F, H | 1, 4, 6
Technology specific data
Water consumption | L/MWh | 1870 | 1870 | 1870 | 1870 | - | - | - | - | I, J | 8, 9, 10, 11
Notes:
A | Assuming gradual improvement to international standard in 2050.
B | Assuming no improvement for regulatory capability.
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998).
D | For economy of scale a proportionality factor of 0.8 is suggested.
E | Uncertainty: Upper is from regulation, Lower is from current standards in Japan (2025) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (upper) for 2025 and +/- 25% for 2050.
G | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | Assuming that costs fall 0.2 % each year.
I | Assuming a cooling tower is used. Pond- and once-through cooling generally result in lower water consumption.
J | Depending on the cooling method, the water consumption can range from around 10 L/MWh to around 2500 L/MWh.
References
1 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Maximum emission from Minister of Environment Regulation 21/2008
4 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016
5 | IEA, World Energy Outlook, 2025
6 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
7 | Danish Energy Agency and Ea Energy Analyses, 2022 - Technology Data for the Indian Power Sector
8 | International Energy Agency, 2016 - Water Energy Nexus
9 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
10 | U.S. Energy Information Administration, 2024 - Thermoelectric cooling water data
11 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Coal ultra-supercritical
Coal ultra-supercritical
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1000 | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
Generating capacity for total power plant | MW_e | 1000 | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
Electrical efficiency, net, name plate | % | 42.5 | 43.8 | 44.4 | 45.1 | 40 | 45 | 42 | 47 |  | 1, 5, 6
Electrical efficiency, net, annual average | % | 41.5 | 42.7 | 43.4 | 44 | 40 | 45 | 42 | 47 |  | 1, 6
Forced outage | % | 7 | 6 | 5 | 3 | 5 | 15 | 2 | 7 | A | 1
Planned outage | % | 13.5 | 9.6 | 7.7 | 5.8 | 5.8 | 15.4 | 3.8 | 7.7 | A | 1
Self-consumption | % | 6 | 6 | 6 | 6 | 5 | 8 | 5 | 8
Technical lifetime | years | 30 | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Construction time | years | 4.33 | 3 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
Space requirement | 1000_m2/MW_e | - | - | - | - | - | - | - | - |  | 6
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
Minimum load | % of full load | 30 | 25 | 22.5 | 20 | 25 | 50 | 10 | 30 | A | 1
Warm start-up time | hours | 4 | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
Cold start-up time | hours | 12 | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Minimum Up time | hours | - | - | - | - | - | - | - | - |  | 7
Minimum Down time | hours | - | - | - | - | - | - | - | - |  | 7
Environment
PM 2.5 | mg/Nm3 | 70 | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2, 3
SO2 (degree of desulphuring) | % | 86 | 86 | 90 | 95 | 73 | 95 | 73 | 95 |  | 2, 3
NOX | g/GJ_i | 152 | 150 | 100 | 38 | 152 | 263 | 38 | 263 | C | 2, 3
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 2.01 | 1.99 | 1.95 | 1.91 | 1.51 | 2.72 | 1.43 | 2.39 | D, F, G, H | 1, 5, 6
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M | USD/MW_e/year | 75311 | 74561 | 73083 | 71634 | 56483 | 101670 | 53726 | 89543 | F, H | 1, 5, 6
Variable O&M | USD/MWh | 1.3 | 1.29 | 1.26 | 1.24 | 0.98 | 1.76 | 0.93 | 1.55 | F, H | 1, 6
Start-up costs | USD/MW_e/start-up | 67 | 67 | 67 | 67 | 50 | 91 | 50 | 84 | F, H | 1, 4, 6
Technology specific data
Water consumption | L/MWh | 1870 | 1870 | 1870 | 1870 | - | - | - | - | I | 8, 9, 10, 11
Notes:
A | Assuming gradual improvement to international standard in 2050.
B | Assuming no improvement for regulatory capability.
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998).
D | For economy of scale a proportionality factor of 0.8 is suggested.
E | Uncertainty: Upper is from regulation, Lower is from current standards in Japan (2025) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
G | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | Assuming that costs fall 0.2 % each year.
I | Ranges for supercritical coal are also valid for ultra-supercritical coal.
References
1 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Maximum emission from Minister of Environment Regulation 21/2008
4 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016
5 | IEA, World Energy Outlook, 2025
6 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
7 | Danish Energy Agency and Ea Energy Analyses, 2022 - Technology Data for the Indian Power Sector
8 | International Energy Agency, 2016 - Water Energy Nexus
9 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
10 | U.S. Energy Information Administration, 2024 - Thermoelectric cooling water data
11 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Coal lifetime extension
Coal lifetime extension
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -1 | -1 | -1 | -1 | 0 | -3 | 0 | -3 | A | 1, 6, 7
Electrical efficiency, net, annual average | % | -1 | -1 | -1 | -1 | 0 | -3 | 0 | -3 | A | 1, 6, 7
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 6
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 1.9 | A | 6
Self-consumption | % | 13.5 | 13.5 | 13.5 | 13.5 | - | - | - | -
Technical lifetime | years | 20 | 20 | 20 | 20 | 10 | 20 | 10 | 20 | A
Construction time | years | - | - | - | - | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3
Environment
PM 2.5 (compared to 100% coal) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 8
SO2 (degree of desulphuring, compared to 100% coal) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 8
NOX (compared to 100% coal) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 8
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.21 | 0.21 | 0.21 | 0.21 | 0.1 | 0.3 | 0.1 | 0.3 | A, B, C | 1, 2
- of which equipment | % | 67 | 67 | 67 | 67 | - | - | - | -
- of which installation and other costs | % | 33 | 33 | 33 | 33 | - | - | - | -
- of which equipment | MUSD/MW_e | 0.14 | 0.14 | 0.14 | 0.14 | - | - | - | -
- of which installation and other costs | MUSD/MW_e | 0.07 | 0.07 | 0.07 | 0.07 | - | - | - | -
Fixed O&M (compared to 100% coal) | % | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | D | 5, 7, 8
Variable O&M (compared to 100% coal) | % | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 |  | 5, 7, 8
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | E
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | It is assumed that plant emissions prior to the LTE are within the legal limits.
C | Investment costs will vary largely, depending on the necessary scope of work. The indicated range represents typical cases where life time is extended to obtain additional 20 years life time.
D | Values depend on those of the plant prior to LTE, however, the average fixed O&M cost may increase slightly for the extension period compared with the original life time to accommodate the necessary reinvestments during the extended life time.
E | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Project for the renovation and upgrade equipment of Pha Lai 1 Thermal Power Plant - Unit 1, Institute of Energy, 2025
2 | GFANZ, ClimateWorks Foundation and Institute of Energy, 2025 - Study on flexibility of coal thermal power plants to support the energy transition in Vietnam
3 | Parsons Brinckerhoff, “Coal and Gas Assumptions,” 2014, https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/315717/coal_and_gas_assumptions.PDF
4 | S. Thomas, “Power-plant life extension,” Energy, vol. 13, no. 10, pp. 767–786, 1988, doi: https://doi.org/10.1016/0360-5442(88)90060-6.
5 | EIA, “Generating Unit Annual Capital and Life Extension Costs Analysis", 2019
6 | Electricity Generation Costs, Department of Energy and Climate Change (UK), Dec 2013. https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/269888/131217_Electricity_Generation_costs_report_December_2013_F inal.pdf
7 | EPRI, Generic guidelines for the life extension of fossil fuel power plants, 1986
8 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity

## Pulverized coal cofiring NH3
Pulverized coal – co-firing 20% ammonia
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -1 | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A, B | 5
Electrical efficiency, net, annual average | % | -1 | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A, B | 5
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | 8.6 | 8.6 | 8.6 | 8.6 | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | - | -
Construction time | years | 1 | 1 | 1 | 1 | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Environment
PM 2.5 (compared to 100% coal) | % | -20 | -20 | -20 | -20 | -10 | -20 | -10 | -20 | A, C | 5
SO2 (degree of desulphuring, compared to 100% coal) | % | -20 | -20 | -20 | -20 | -10 | -20 | -10 | -20 | A, D | 5
NOX (compared to 100% coal) | % | 5 | 5 | 5 | 5 | 0 | 10 | 0 | 10 | A, E | 3, 5, 6, 7
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 | A, F, G | 1, 2, 4
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M (compared to 100% coal) | % | 5 | 5 | 5 | 5 | 3 | 8 | 3 | 8 | A | 3, 4
Variable O&M (compared to 100% coal) | % | 5 | 5 | 5 | 5 | 3 | 8 | 3 | 8 | A | 3, 4
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | H
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | 100mg/Nm3 (at 6% O2), 20% reduction compared to firing coal.
D | 500mg/Nm3 (at 6% O2), 20% reduction compared to firing coal.
E | Assuming it remains the same as when firing coal.
F | The nominal investment assumes that investment for a general life time extension campaign is excluded.
G | The investment cost includes modifying existing coal plants for ammonia co-firing which requires boiler modifications and investment in additional facilities like ammonia tanks and vaporizers. In general, the retrofits include [3]: Modified burner; New ammonia receiving device, pipe, tank and vaporizer; Additional NOx removal device. The cost of improving pipelines outside the plant-land plot is not included.
H | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Fuel conversion project for Unit 2 of Pha lai thermal power plant, Institute of Energy, 2025
2 | GFANZ, ClimateWorks Foundation and Institute of Energy, 2025 - Study on flexibility of coal thermal power plants to support the energy transition in Vietnam
3 | BloombergNEF, 2022 - Japan’s costly ammonia coal co-firing strategy
4 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
5 | G.Nagatani, H.Ishii, T.Ito, E.Ohno, Y.Okuma, 2020 - Development of Co-firing method of Pulverized coal and Ammonia to reduce greenhouse gas emissions. IHI Engineering Review, Vol.53, No.1, 2020
6 | T. Ito, H.Ishii, J.Zhang, S..Ishihara, S.Toshiyuki (IHI Corporation), New technology of the Ammonia co-firing with pulverized coal to reduce the NOx emission. AIChE meeting 2019
7 | J.Tan, Y.He, R.Zhu, Y.Zhu, Z.Wang, Experimental study on co-firing characteristic of ammonia with pulverized coal in a staged combustion drop tube furnace, 2022
Pulverized coal – co-firing 100% ammonia
Parameter | Unit | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -2 | -2 | -2 | -1 | -3 | -1 | -3 | A, B | 5
Electrical efficiency, net, annual average | % | -2 | -2 | -2 | -1 | -3 | -1 | -3 | A, B | 5
Forced outage | % | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | 8.6 | 8.6 | 8.6
Technical lifetime | years
Construction time | years | 1 | 1 | 1
Space requirement (additional to existing plant) | 1000_m2/MW_e
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Environment
PM 2.5 (compared to 100% coal) | % | -100 | -100 | -100 | -70 | -100 | -70 | -100 | A, C | 5
SO2 (degree of desulphuring, compared to 100% coal) | % | -100 | -100 | -100 | -70 | -100 | -70 | -100 | A, D | 5
NOX (compared to 100% coal) | % | 30 | 30 | 30 | 20 | 50 | 20 | 50 | A, E | 3, 5, 6, 7
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.35 | 0.35 | 0.35 | 0.2 | 0.6 | 0.2 | 0.6 | A, F, G | 1, 2, 4
- of which equipment | %
- of which installation and other costs | %
- of which equipment | MUSD/MW_e
- of which installation and other costs | MUSD/MW_e
Fixed O&M (compared to 100% coal) | % | 10 | 10 | 10 | 5 | 15 | 5 | 15 | A | 3, 4
Variable O&M (compared to 100% coal) | % | 10 | 10 | 10 | 5 | 15 | 5 | 15 | A | 3, 4
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | - | H
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | 100mg/Nm3 (at 6% O2), 100% reduction compared to firing coal.
D | 500mg/Nm3 (at 6% O2), 100% reduction compared to firing coal.
E | Assuming it remains the same as when firing coal.
F | The nominal investment assumes that investment for a general life time extension campaign is excluded.
G | The investment cost includes modifying existing coal plants for ammonia co-firing which requires boiler modifications and investment in additional facilities like ammonia tanks and vaporizers. In general, the retrofits include [3]: Modified burner; New ammonia receiving device, pipe, tank and vaporizer; Additional NOx removal device. The cost of improving pipelines outside the plant-land plot is not included.
H | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Fuel conversion project for Unit 2 of Pha lai thermal power plant, Institute of Energy, 2025
2 | GFANZ, ClimateWorks Foundation and Institute of Energy, 2025 - Study on flexibility of coal thermal power plants to support the energy transition in Vietnam
3 | BloombergNEF, 2022 - Japan’s costly ammonia coal co-firing strategy
4 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
5 | G.Nagatani, H.Ishii, T.Ito, E.Ohno, Y.Okuma, 2020 - Development of Co-firing method of Pulverized coal and Ammonia to reduce greenhouse gas emissions. IHI Engineering Review, Vol.53, No.1, 2020
6 | T. Ito, H.Ishii, J.Zhang, S..Ishihara, S.Toshiyuki (IHI Corporation), New technology of the Ammonia co-firing with pulverized coal to reduce the NOx emission. AIChE meeting 2019
7 | J.Tan, Y.He, R.Zhu, Y.Zhu, Z.Wang, Experimental study on co-firing characteristic of ammonia with pulverized coal in a staged combustion drop tube furnace, 2022

## Pulverized coal cofiring biomas
Pulverized coal – co-firing 20% biomass (wood pellets)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -1 | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A, B
Electrical efficiency, net, annual average | % | -1 | -1 | -1 | -1 | 0 | -2 | 0 | -2 | A, B
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | 13.5 | 13.5 | 13.5 | 13.5 | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | - | -
Construction time | years | 1 | 1 | 1 | 1 | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | 0 | 0 | 0 | 0 | - | - | - | - | A, C
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Environment
PM 2.5 (compared to 100% coal) | % | -10 | -10 | -10 | -10 | -5 | -20 | -5 | -20 | A | 2
SO2 (degree of desulphuring, compared to 100% coal) | % | -10 | -10 | -10 | -10 | -5 | -20 | -5 | -20 | A | 2
NOX (compared to 100% coal) | % | -5 | -5 | -5 | -5 | 0 | -10 | 0 | -10 | A | 2
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.16 | 0.16 | 0.16 | 0.16 | 0.05 | 0.3 | 0.05 | 0.3 | A, D | 1
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M (compared to 100% coal) | % | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 2
Variable O&M (compared to 100% coal) | % | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 2
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | E
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | Some additional under roof space (or silos) are required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
D | The nominal investment is excluding investment for a general life time extension campaign.
E | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Fuel conversion project for Unit 1 of Pha lai thermal power plant, Institute of Energy, 2025
2 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
3 | IRENA, “Biomass Co-firing: Technology brief”, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-Brief-E21-Biomass-Co-firing.pdf
4 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055
5 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012
Pulverized coal – co-firing 100% biomass (wood pellets)
Parameter | Unit | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -2 | -2 | -2 | -1 | -3 | -1 | -3 | A, B
Electrical efficiency, net, annual average | % | -2 | -2 | -2 | -1 | -3 | -1 | -3 | A, B
Forced outage | % | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | 8.6 | 8.6 | 8.6
Technical lifetime | years
Construction time | years | 1 | 1 | 1
Space requirement (additional to existing plant) | 1000_m2/MW_e | [7 empty] | A,C
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 2
Environment
PM 2.5 (compared to 100% coal) | % | -70 | -70 | -70 | -50 | -90 | -50 | -90 | A | 2
SO2 (degree of desulphuring, compared to 100% coal) | % | -70 | -70 | -70 | -50 | -90 | -50 | -90 | A | 2
NOX (compared to 100% coal) | % | -30 | -30 | -30 | -5 | -40 | -5 | -40 | A | 2
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.36 | 0.36 | 0.36 | 0.3 | 0.8 | 0.3 | 0.8 | A, D | 1
- of which equipment | %
- of which installation and other costs | %
- of which equipment | MUSD/MW_e
- of which installation and other costs | MUSD/MW_e
Fixed O&M (compared to 100% coal) | % | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 2
Variable O&M (compared to 100% coal) | % | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 2
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | - | E
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | Some additional under roof space (or silos) are required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
D | The nominal investment is excluding investment for a general life time extension campaign.
E | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Fuel conversion project for Unit 1 of Pha lai thermal power plant, Institute of Energy, 2025
2 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
3 | “Biomass Co-firing: Technology brief,” IRENA, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-Brief-E21-Biomass-Co-firing.pdf
4 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055
5 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012

## CFB ultra-supercritical coal
CFB boiler power plant ultra-supercritical
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 600 | 300 | 660 | 300 | 800 |  | 1
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 1200 | 300 | 1200 | 300 | 1800 |  | 1
Electrical efficiency, net, name plate | % | 41 | 42 | 43 | 43 | 37 | 43 | 39 | 45 |  | 1, 5, 6
Electrical efficiency, net, annual average | % | 40 | 41 | 42 | 42 | 37 | 43 | 39 | 45 |  | 1, 6
Forced outage | % | 7 | 6 | 5 | 3 | 5 | 15 | 2 | 7 | A | 1
Planned outage | % | 13 | 10 | 8 | 6 | 6 | 15 | 4 | 8 | A | 1
Self-consumption | % | - | - | - | - | - | - | - | -
Technical lifetime | years | 30 | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
Construction time | years | 3.75 | 3 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
Space requirement | 1000_m2/MW_e | - | - | - | - | - | - | - | - |  | 6
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 4 | 4 | 4 | 4 | 2 | 4 | 3 | 4 | B | 1
Minimum load | % of full load | 40 | 25 | 22.5 | 20 | 25 | 50 | 10 | 30 | A | 1
Warm start-up time | hours | 8 | 4 | 4 | 4 | 2 | 8.5 | 2 | 5 | B | 1
Cold start-up time | hours | 10 | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Minimum Up time | hours | 6 | 6 | 6 | 6 | - | - | - | - |  | 7
Minimum Down time | hours | 4 | 4 | 4 | 4 | - | - | - | - |  | 7
Environment
PM 2.5 | mg/Nm3 | 70 | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2, 3
SO2 (degree of desulphuring) | % | 90 | 90 | 90 | 95 | 90 | 95 | 90 | 99 |  | 2, 3
NOX | g/GJ_i | 108 | 105 | 72 | 38 | 108 | 263 | 38 | 263 | C | 2, 3
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 1.9 | 1.88 | 1.85 | 1.81 | 1.43 | 2.57 | 1.36 | 2.26 | D, F, G, H | 1, 5, 6
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M | USD/MW_e/year | 50920 | 50413 | 49413 | 48434 | 38190 | 68742 | 36326 | 60543 | F, H | 1, 5, 6
Variable O&M | USD/MWh | 1.3 | 1.39 | 1.36 | 1.33 | 0.98 | 1.76 | 1 | 1.66 | F, H | 1, 6
Start-up costs | USD/MW_e/start-up | 65 | 65 | 65 | 65 | 49 | 87 | 49 | 81 | F, H | 1, 4, 6
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | I
Notes:
A | Assuming gradual improvement to international standard in 2050.
B | Assuming no improvement for regulatory capability.
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998).
D | For economy of scale a proportionality factor of 0.8 is suggested.
E | Uncertainty: Upper is from regulation, Lower is from current standards in Japan (2025) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
G | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
H | Assuming that costs fall 0.2 % each year.
I | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Maximum emission from Minister of Environment Regulation 21/2008
4 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016
5 | IEA, World Energy Outlook, 2025
6 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
7 | Danish Energy Agency and Ea Energy Analyses, 2022 - Technology Data for the Indian Power Sector

## CFB coal cofiring biomas
CFB coal – co-firing 20% biomass (wood pellets, wood chips)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 300 | 300 | 300 | 300 | 150 | 600 | 150 | 600
Generating capacity for total power plant | MW_e | 600 | 600 | 600 | 600 | 300 | 1200 | 300 | 1200
Electrical efficiency, net, name plate | % | 0 | 0 | 0 | 0 | 0 | -1 | 0 | -1 | A, B | 3,14,15
Electrical efficiency, net, annual average | % | 0 | 0 | 0 | 0 | 0 | -1 | 0 | -1 | A, B | 3,14,15
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 3,14,15
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Self-consumption | % | - | - | - | - | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | - | -
Construction time | years | 1 | 1 | 1 | 1 | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | 0 | 0 | 0 | 0 | - | - | - | - | A, C | 3,14,15
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Environment
PM 2.5 (compared to 100% coal) | % | -10 | -10 | -10 | -10 | -5 | -20 | -5 | -20 | A | 1,2
SO2 (degree of desulphuring, compared to 100% coal) | % | -10 | -10 | -10 | -10 | -5 | -20 | -5 | -20 | A | 1,2
NOX (compared to 100% coal) | % | -5 | -5 | -5 | -5 | 0 | -10 | 0 | -10 | A | 1,2
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.06 | 0.06 | 0.06 | 0.06 | 0.01 | 0.2 | 0.01 | 0.2 | A, D | 1, 2
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M (compared to 100% coal) | % | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 3,14,15
Variable O&M (compared to 100% coal) | % | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 3,14,15
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | E
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as for the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
D | The nominal investment is excluding investment for a general life time extension campaign.
E | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Institute of Energy, 2025 - Report on study and assessment of biomass and coal co-firing technology in coal-fired thermal power plants in Vietnam (Na Duong Thermal Power Plant)
2 | GFANZ, ClimateWorks Foundation and Institute of Energy, 2025 - Study on flexibility of coal thermal power plants to support the energy transition in Vietnam
3 | IRENA, “Biomass Co-firing: Technology brief”, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-BriefE21-Biomass-Co-firing.pdf
4 | M. V Gil and F. Rubiera, “5 - Coal and biomass cofiring: fundamentals and future trends,” in New Trends in Coal Conversion, I. Suárez-Ruiz, M. A. Diez, and F. Rubiera, Eds. Woodhead Publishing, 2019, pp. 117–140. doi: https://doi.org/10.1016/B978-0-08-102201-6.00005-4
5 | Y. Xu, K. Yang, J. Zhou, and G. Zhao, “Coal-Biomass Co-Firing Power Generation Technology: Current Status, Challenges and Policy Implications, ”Sustainability, vol. 12, no. 9, 2020, doi: 10.3390/su12093692
6 | M. v. Gil and F. Rubiera, “Coal and biomass cofiring: fundamentals and future trends,” in New Trends in Coal Conversion: Combustion, Gasification, Emissions, and Coking, Elsevier, 2018, pp. 117–140. doi: 10.1016/B978-0-08-102201-6.00005-4
7 | M. Ashizawa, M. Otaka, H. Yamamoto, and A. Akisawa, “CO2 Emissions and Economy of Co-Firing Carbonized Wood Pellets at Coal-Fired Power Plants: The Case of Overseas Production of Pellets and Use in Japan,” Energies, vol. 15, no. 5, 2022, doi: 10.3390/en15051770.
8 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055
9 | S. Mehmood, B. V Reddy, and M. A. Rosen, “Energy Analysis of a Biomass Co-firing Based Pulverized Coal Power Generation System,” Sustainability, vol. 4, no. 4, pp. 462–490, 2012, doi: 10.3390/su4040462
10 | M. S. Roni, S. Chowdhury, S. Mamun, M. Marufuzzaman, W. Lein, and S. Johnson, “Biomass co-firing technology with policies, challenges, and opportunities: A global review,” Renewable and Sustainable Energy Reviews, vol. 78, pp. 1089–1101, 2017, doi: 60 https://doi.org/10.1016/j.rser.2017.05.023
11 | Biomass pelleting, European Biomass Industry Association, 2015. http://www.eubia.org/index.php/about-biomass/biomass-pelleting
12 | Macalister, Terry (30 May 2011). "RWE to convert Tilbury power station into biomass plant". The Guardian. Retrieved 30 August 2011
13 | Information collected from Ninh Binh power plants
14 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012
15 | Danish Energy Agency and Energinet, “Technology Data - Energy Plants for Electricity and District heating generation”, 2016
CFB coal – co-firing 100% biomass (wood pellets, wood chips)
Parameter | Unit | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 600 | 600 | 600 | 300 | 1000 | 300 | 1000
Generating capacity for total power plant | MW_e | 1200 | 1200 | 1200 | 300 | 2000 | 300 | 2000
Electrical efficiency, net, name plate | % | -1 | -1 | -1 | -1 | -2 | -1 | -2 | A, B | 3,14,15
Electrical efficiency, net, annual average | % | -1 | -1 | -1 | -1 | -2 | -1 | -2 | A, B | 3,14,15
Forced outage | % | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A | 3,14,15
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Self-consumption | % | 8.6 | 8.6 | 8.6 | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | -
Construction time | years | 1 | 1 | 1 | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | - | - | - | - | - | - | - | A, C | 3,14,15
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum Up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Minimum Down time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 3,14,15
Environment
PM 2.5 (compared to 100% coal) | % | -70 | -70 | -70 | -50 | -90 | -50 | -90 | A | 1,2
SO2 (degree of desulphuring, compared to 100% coal) | % | -70 | -70 | -70 | -50 | -90 | -50 | -90 | A | 1,2
NOX (compared to 100% coal) | % | -30 | -30 | -30 | -5 | -40 | -5 | -40 | A | 1,2
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.29 | 0.29 | 0.29 | 0.15 | 0.5 | 0.15 | 0.5 | A, D | 1,2
- of which equipment | % | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | -
Fixed O&M (compared to 100% coal) | % | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 3,14,15
Variable O&M (compared to 100% coal) | % | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 3,14,15
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | - | E
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as for the parameter).
B | Typically, the electrical efficiency is 1-2 % point lower than that of the plant prior to conversion.
C | Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
D | The nominal investment is excluding investment for a general life time extension campaign.
E | Assuming the same plant is used as stated the for Supercritical Coal Power Plant.
References
1 | Institute of Energy, 2025 - Report on study and assessment of biomass and coal co-firing technology in coal-fired thermal power plants in Vietnam (Na Duong Thermal Power Plant)
2 | GFANZ, ClimateWorks Foundation and Institute of Energy, 2025 - Study on flexibility of coal thermal power plants to support the energy transition in Vietnam
3 | IRENA, “Biomass Co-firing: Technology brief”, 2013. https://irena.org/-/media/Files/IRENA/Agency/Publication/2013/IRENA-ETSAP-Tech-BriefE21-Biomass-Co-firing.pdf
4 | M. V Gil and F. Rubiera, “5 - Coal and biomass cofiring: fundamentals and future trends,” in New Trends in Coal Conversion, I. Suárez-Ruiz, M. A. Diez, and F. Rubiera, Eds. Woodhead Publishing, 2019, pp. 117–140. doi: https://doi.org/10.1016/B978-0-08-102201-6.00005-4
5 | Y. Xu, K. Yang, J. Zhou, and G. Zhao, “Coal-Biomass Co-Firing Power Generation Technology: Current Status, Challenges and Policy Implications,” Sustainability, vol. 12, no. 9, 2020, doi: 10.3390/su12093692
6 | M. v. Gil and F. Rubiera, “Coal and biomass cofiring: fundamentals and future trends,” in New Trends in Coal Conversion: Combustion, Gasification, Emissions, and Coking, Elsevier, 2018, pp. 117–140. doi: 10.1016/B978-0-08-102201-6.00005-4
7 | M. Ashizawa, M. Otaka, H. Yamamoto, and A. Akisawa, “CO2 Emissions and Economy of Co-Firing Carbonized Wood Pellets at Coal-Fired Power Plants: The Case of Overseas Production of Pellets and Use in Japan,” Energies, vol. 15, no. 5, 2022, doi: 10.3390/en15051770
8 | X. Wang et al., “Experimental investigation on biomass co-firing in a 300MW pulverized coal-fired utility furnace in China,” Proceedings of the Combustion Institute, vol. 33, no. 2, pp. 2725–2733, 2011, doi: https://doi.org/10.1016/j.proci.2010.06.055.
9 | S. Mehmood, B. V Reddy, and M. A. Rosen, “Energy Analysis of a Biomass Co-firing Based Pulverized Coal Power Generation System,” Sustainability, vol. 4, no. 4, pp. 462–490, 2012, doi: 10.3390/su4040462
10 | M. S. Roni, S. Chowdhury, S. Mamun, M. Marufuzzaman, W. Lein, and S. Johnson, “Biomass co-firing technology with policies, challenges, and opportunities: A global review,” Renewable and Sustainable Energy Reviews, vol. 78, pp. 1089–1101, 2017, doi: 60 https://doi.org/10.1016/j.rser.2017.05.023
11 | Biomass pelleting, European Biomass Industry Association, 2015. http://www.eubia.org/index.php/about-biomass/biomass-pelleting
12 | Macalister, Terry (30 May 2011). "RWE to convert Tilbury power station into biomass plant". The Guardian. Retrieved 30 August 2011
13 | Information collected from Ninh Binh power plants
14 | Rohan Fernando, IEA Clean Coal Centre, “Cofiring high ratios of biomass with coal”, 2012
15 | Danish Energy Agency and Energinet, “Technology Data - Energy Plants for Electricity and District heating generation”, 2016

## SCGT
Simple Cycle Gas Turbine - large system
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 510 | 510 | 510 | 510 | 250 | 750 | 250 | 750 |  | 1
Generating capacity for total power plant | MW_e | 510 | 510 | 510 | 510 | 250 | 750 | 250 | 750 |  | 1
Electrical efficiency, net, name plate | % | 42 | 43 | 45 | 46 | 35 | 45 | 39 | 49 |  | 1
Electrical efficiency, net, annual average | % | 41 | 42 | 44 | 45 | 34 | 44 | 38 | 48
Forced outage | % | 2 | 2 | 2 | 2 | 1.5 | 10 | 1.5 | 10 |  | 1
Planned outage | % | 3 | 3 | 3 | 3 | 2.5 | 10 | 2.5 | 10 |  | 1
Self-consumption | % | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 3 | 1.8 | 3 |  | 1
Technical lifetime | years | 50 | 50 | 50 | 50 | 20 | 60 | 20 | 60 |  | 1
Construction time | years | 3 | 3 | 3 | 3 | 2.5 | 4 | 2.5 | 4 |  | 1
Space requirement | 1000_m2/MW_e | 0.36 | 0.36 | 0.36 | 0.36 | 0.2 | 0.6 | 0.2 | 0.6 |  | 1
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 15 | 20 | 20 | 20 | 10 | 30 | 10 | 30
Minimum load | % of full load | 33 | 30 | 25 | 15 | 25 | 50 | 10 | 40 |  | 1
Warm start-up time | hours | 0.35 | 0.2 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4
Cold start-up time | hours | 0.75 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1
Minimum Up time | hours | 4 | 4 | 4 | 4 | - | - | - | -
Minimum Down time | hours | 3 | 3 | 3 | 3 | - | - | - | -
Environment
PM 2.5 | mg/Nm3 | 15 | 15 | 15 | 15 | - | - | - | - |  | 1
SO2 | mg/Nm3 | 60 | 60 | 60 | 60 | - | - | - | - |  | 1
NOX | g/GJ_i | 78 | 60 | 40 | 20 | 20 | 86 | 20 | 86
CH4 | mg/Nm3 | - | - | - | - | - | - | - | -
N2O | mg/Nm3 | 51 | 51 | 51 | 51 | - | - | - | - |  | 1
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 1.02 | 1.01 | 0.99 | 0.97 | 0.77 | 1.38 | 0.73 | 1.21 | A | 2, 3, 4
- of which equipment | % | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 8
- of which installation and other costs | % | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 8
- of which equipment | MUSD/MW_e | 0.51 | 0.5 | 0.49 | 0.49 | 0.38 | 0.69 | 0.36 | 0.61 | A | 8
- of which installation and other costs | MUSD/MW_e | 0.51 | 0.5 | 0.49 | 0.49 | 0.38 | 0.69 | 0.36 | 0.61 | A | 8
Fixed O&M | USD/MW_e/year | 30004 | 29705 | 29116 | 28539 | 22503 | 40506 | 21405 | 35674 | A | 2, 3, 4
Variable O&M | USD/MWh | 4.58 | 4.53 | 4.44 | 4.36 | 3.44 | 6.18 | 3.27 | 6 | A
Start-up costs | USD/MW_e/start-up | 31.1 | 31.1 | 31.1 | 31.1 | 23.3 | 41.9 | 23.3 | 38.8 | A | 5
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | B | 9, 10, 11
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Since no cooling water is needed, the water consumption is negligible.
References
1 | Based on projects from Vietnam
2 | IEA, Projected Costs of Generating Electricity, 2020
3 | IEA, World Energy Outlook, 2025
4 | Danish Energy Agency, "Technology Catalogue on Power and Heat Generation", 2025
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016
6 | Maximum emission from Minister of Environment of Indonesia, Regulation 21/2008.
7 | Vuorinen, A., "Planning of Optimal Power Systems", 2008.
8 | Soares, "Gas Turbines: A Handbook of Air, Land and Sea Applications", 2008.
9 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025
10 | Cambridge university press, 2012 - The energy–water nexus: Water use trends in sustainable energy and opportunities for materials research and development
11 | Union of concerned scientists, 2013 - How it Works: Water for Natural Gas

## CCGT
Combined Cycle Gas Turbine
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 750 | 750 | 750 | 750 | 200 | 800 | 200 | 800 |  | 1, 2
Generating capacity for total power plant | MW_e | 1500 | 1500 | 1500 | 1500 | 200 | 1600 | 200 | 1600 |  | 1, 2
Electrical efficiency, net, name plate | % | 58 | 60 | 61 | 61 | 45 | 62 | 55 | 65 |  | 1, 2, 4, 5, 10
Electrical efficiency, net, annual average | % | 56 | 58 | 59 | 59 | 39 | 61 | 54 | 64
Forced outage | % | 2 | 2 | 2 | 2 | 1.5 | 10 | 1.5 | 10 |  | 1
Planned outage | % | 3 | 3 | 3 | 3 | 2.5 | 10 | 2.5 | 10 |  | 1
Self-consumption | % | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
Technical lifetime | years | 50 | 50 | 50 | 50 | 20 | 60 | 20 | 60 |  | 1
Construction time | years | 3.5 | 3.5 | 3.5 | 3.5 | 2.5 | 4 | 2.5 | 4 |  | 1
Space requirement | 1000_m2/MW_e | 0.36 | 0.36 | 0.36 | 0.36 | 0.2 | 0.6 | 0.2 | 0.6 |  | 1
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 11.7 | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 1
Minimum load | % of full load | 33 | 30 | 25 | 15 | 25 | 50 | 10 | 40 |  | 1
Warm start-up time | hours | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 1 | 1.5 |  | 1
Cold start-up time | hours | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 4 | 2 | 4
Minimum Up time | hours | 4 | 4 | 4 | 4 | - | - | - | -
Minimum Down time | hours | 3 | 3 | 3 | 3 | - | - | - | -
Environment
PM 2.5 | mg/Nm3 | 15 | 15 | 15 | 15 | - | - | - | - |  | 1
SO2 | mg/Nm3 | 60 | 60 | 60 | 60 | - | - | - | - |  | 1
NOX | g/GJ_i | 78 | 60 | 40 | 20 | 20 | 86 | 20 | 86 |  | 7, 8
CH4 | mg/Nm3 | - | - | - | - | - | - | - | -
N2O | mg/Nm3 | 51 | 51 | 51 | 51 | - | - | - | - |  | 1
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 1.15 | 1.14 | 1.12 | 1.09 | 0.86 | 1.55 | 0.82 | 1.37 | A | 1, 2, 4, 10
- of which equipment | % | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 1, 9
- of which installation and other costs | % | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 1, 9
- of which equipment | MUSD/MW_e | 0.58 | 0.57 | 0.56 | 0.55 | 0.43 | 0.78 | 0.41 | 0.68 | A
- of which installation and other costs | MUSD/MW_e | 0.58 | 0.57 | 0.56 | 0.55 | 0.43 | 0.78 | 0.41 | 0.68 | A
Fixed O&M | USD/MW_e/year | 42326 | 41904 | 41074 | 40260 | 31744 | 57140 | 30195 | 50324 | A | 1, 2, 4
Variable O&M | USD/MWh | 2.48 | 2.46 | 2.41 | 2.36 | 1.86 | 3.35 | 1.77 | 2.95 | A | 1
Start-up costs | USD/MW_e/start-up | 87 | 87 | 87 | 87 | 65 | 117 | 65 | 108 | A
Technology specific data
Water consumption | L/MWh | 750 | 750 | 750 | 750 | - | - | - | - | B | 11, 12, 13
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming a cooling tower is used. Pond-cooling, once-through cooling and dry cooling can also be used. Dry cooling has the lowest water consumption, and the other methods are generally not very far from tower-cooling. The water consumption can vary in the range 100-1000 L/MWh.
References
1 | Based on projects in Vietnam
2 | Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024.
3 | Vuorinen, A., "Planning of Optimal Power Systems", 2008.
4 | IEA, World Energy Outlook, 2025.
5 | Siemens, "Flexible future for combined cycle", 2010.
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment of Indonesia, Regulation 21/2008.
8 | Danish Energy Agency, "Technology Catalogue on Power and Heat Generation", 2025.
9 | Soares, "Gas Turbines: A Handbook of Air, Land and Sea Applications", 2008
10 | IEA, Projected Costs of Generating Electricity, 2020.
11 | International Energy Agency, 2016 - Water Energy Nexus
12 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
13 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025

## CCGT cofiring hydrogen
CCGT – co-firing 20% hydrogen (in terms of energy)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 750 | 750 | 750 | 750 | 200 | 800 | 200 | 800
Generating capacity for total power plant | MW_e | 1500 | 1500 | 1500 | 1500 | 200 | 1600 | 200 | 1600
Electrical efficiency, net, name plate | % | 0 | 0 | 0 | 0 | 0 | -2 | 0 | -2 | A | 3, 9
Electrical efficiency, net, annual average | % | 0 | 0 | 0 | 0 | 0 | -2 | 0 | -2 | A | 3, 9
Forced outage | % | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | - | - | - | - | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | - | -
Construction time | years | - | - | - | - | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Minimum load | % of full load | -3 | -3 | -3 | -3 | -1 | -5 | -1 | -5 | A | 1, 2, 3, 6
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Minimum Up time | hours | - | - | - | - | - | - | - | -
Minimum Down time | hours | - | - | - | - | - | - | - | -
Environment
PM 2.5 (compared to 100% coal) | % | -20 | -20 | -20 | -20 | -10 | -20 | -10 | -20 | A | 1, 2, 6
SO2 (degree of desulphuring, compared to 100% coal) | % | -20 | -20 | -20 | -20 | -10 | -20 | -10 | -20 | A | 1, 2, 6
NOX (compared to 100% coal) | % | 20 | 20 | 20 | 20 | 10 | 60 | 10 | 60 | A | 1, 2, 6, 9, 10, 11, 12
CH4 | % | - | - | - | - | - | - | - | -
N2O | % | - | - | - | - | - | - | - | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.07 | 0.07 | 0.07 | 0.07 | 0.04 | 0.12 | 0.04 | 0.12 | A, B | 1, 2, 4
- of which equipment | % | - | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | - | -
Fixed O&M | USD/MW_e/year | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 1, 2, 4
Variable O&M | USD/MWh | 3 | 3 | 3 | 3 | 1 | 5 | 1 | 5 | A | 1, 2, 4
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | - | - | - | - | C
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | The nominal investment assumes that exclude investment for a general lifetime extension campaign.
C | Assuming that the same plant is used as for Combined Cycle Gas Turbine.
References
1 | Anas Abuzayed, Michael G. Pollitt, Mario Liebensteiner, Simone Hochgreb, “Exploring the feasibility of low-carbon fuel blends in CCGTs for deep decarbonization of power systems”, 2026
2 | VGBE, “Factsheet H2-readiness for gas turbine plants”, 2023
3 | “Hydrogen gas turbines,” ETN Global, 2020. https://etn.global/wp-content/uploads/2020/01/ETN-Hydrogen-Gas-Turbines-report.pdf
4 | S. Öberg, M. Odenberger, and F. Johnsson, “Exploring the competitiveness of hydrogen-fueled gas turbines in future energy systems,” Int. J. Hydrogen Energy, vol. 47, no. 1, pp. 624–644, 2022, doi: https://doi.org/10.1016/j.ijhydene.2021.10.035
5 | GE, “POWER TO GAS: HYDROGEN FOR POWER GENERATION,” 2019. https://www.ge.com/content/dam/gepower/global/en_US/documents/fuel-flexibility/GEA33861 Power to Gas - Hydrogen for Power Generation.pdf
6 | EPRI, “Hydrogen-Capable Gas Turbines for Deep Decarbonization,” 2019. https://h2fcp.org/sites/default/files/3002017544_Technology-Insights-Brief_ Hydrogen_Capable-Gas-Turbines-for-Deep-Decarbonization.pdf
7 | “Hanwha wins hydrogen co-firing gas turbine remodeling project in the US,” Hanwha, 2021. http://www.koreaittimes.com/news/articleView.html?idxno=109812
8 | IEA, “The role of low-carbon fuels in the clean energy transitions of the power sector”, 2022
9 | T.Wind, F.Guthe, K.Syed, “Co-firing of hydrogen and natural gases in lean premixed conventional and reheat burners (Alstom GT26), 2014
10 | L.Wright, C.Lewis, “Emission of NOx from blending of hydrogen and natural gas in space heating boilers”, 2022
11 | Georgia Tech/Strategic Energy Institute, “NOx emission from Hydrogen_Methane fuel blends”, 2022
12 | GE, "Powering to a cleaner energy future with hydrogen”, 2022
CCGT – co-firing 100% hydrogen (in terms of energy)
Parameter | Unit | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 750 | 750 | 750 | 200 | 800 | 200 | 800
Generating capacity for total power plant | MW_e | 1500 | 1500 | 1500 | 200 | 1600 | 200 | 1600
Electrical efficiency, net, name plate | % | 0 | 0 | 0 | 0 | -3 | 0 | -3 | A | 3, 9
Electrical efficiency, net, annual average | % | 0 | 0 | 0 | 0 | -3 | 0 | -3 | A | 3, 9
Forced outage | % | 0 | 0 | 0 | 0 | 1 | 0 | 1 | A
Planned outage | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A
Self-consumption | % | - | - | - | - | - | - | -
Technical lifetime | years | - | - | - | - | - | - | -
Construction time | years | - | - | - | - | - | - | -
Space requirement (additional to existing plant) | 1000_m2/MW_e | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Minimum load | % of full load | -5 | -5 | -5 | -3 | -10 | -3 | -10 | A | 1, 2, 3, 6
Warm start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Cold start-up time | hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | 1, 2, 3, 6
Minimum Up time | hours | - | - | - | - | - | - | -
Minimum Down time | hours | - | - | - | - | - | - | -
Environment
PM 2.5 (compared to 100% coal) | % | -100 | -100 | -100 | -100 | -100 | -100 | -100 | A | 1, 2, 6
SO2 (degree of desulphuring, compared to 100% coal) | % | -100 | -100 | -100 | -100 | -100 | -100 | -100 | A | 1, 2, 6
NOX (compared to 100% coal) | % | 40 | 40 | 40 | 20 | 100 | 20 | 100 | A | 1, 2, 6, 9, 10, 11, 12
CH4 | % | - | - | - | - | - | - | -
N2O | % | - | - | - | - | - | - | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.24 | 0.24 | 0.24 | 0.18 | 0.3 | 0.18 | 0.3 | A, B | 1, 2, 4
- of which equipment | % | - | - | - | - | - | - | -
- of which installation and other costs | % | - | - | - | - | - | - | -
- of which equipment | MUSD/MW_e | - | - | - | - | - | - | -
- of which installation and other costs | MUSD/MW_e | - | - | - | - | - | - | -
Fixed O&M | USD/MW_e/year | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 1, 2, 4
Variable O&M | USD/MWh | 5 | 5 | 5 | 3 | 10 | 3 | 10 | A | 1, 2, 4
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | - | C
Notes:
A | Value depends on the original plant. Value indicates the estimated change from the original value (unit is the same as the parameter).
B | The nominal investment assumes that exclude investment for a general lifetime extension campaign.
C | Assuming that the same plant is used as for Combined Cycle Gas Turbine.
References
1 | Anas Abuzayed, Michael G. Pollitt, Mario Liebensteiner, Simone Hochgreb, “Exploring the feasibility of low-carbon fuel blends in CCGTs for deep decarbonization of power systems”, 2026
2 | VGBE, “Factsheet H2-readiness for gas turbine plants”, 2023
3 | “Hydrogen gas turbines,” ETN Global, 2020. https://etn.global/wp-content/uploads/2020/01/ETN-Hydrogen-Gas-Turbines-report.pdf
4 | S. Öberg, M. Odenberger, and F. Johnsson, “Exploring the competitiveness of hydrogen-fueled gas turbines in future energy systems,” Int. J. Hydrogen Energy, vol. 47, no. 1, pp. 624–644, 2022, doi: https://doi.org/10.1016/j.ijhydene.2021.10.035
5 | GE, “POWER TO GAS: HYDROGEN FOR POWER GENERATION,” 2019. https://www.ge.com/content/dam/gepower/global/en_US/documents/fuel-flexibility/GEA33861 Power to Gas - Hydrogen for Power Generation.pdf
6 | EPRI, “Hydrogen-Capable Gas Turbines for Deep Decarbonization,” 2019. https://h2fcp.org/sites/default/files/3002s017544_Technology-Insights-Brief_ Hydrogen_Capable-Gas-Turbines-for-Deep-Decarbonization.pdf
7 | “Hanwha wins hydrogen co-firing gas turbine remodeling project in the US,” Hanwha, 2021. http://www.koreaittimes.com/news/articleView.html?idxno=109812
8 | IEA, “The role of low-carbon fuels in the clean energy transitions of the power sector”, 2022
9 | T.Wind, F.Guthe, K.Syed, “Co-firing of hydrogen and natural gases in lean premixed conventional and reheat burners (Alstom GT26), 2014
10 | L.Wright, C.Lewis, “Emission of NOx from blending of hydrogen and natural gas in space heating boilers”, 2022
11 | Georgia Tech/Strategic Energy Institute, “NOx emission from Hydrogen_Methane fuel blends”, 2022
12 | GE, "Powering to a cleaner energy future with hydrogen”, 2022

## Coal CCS
Supercritical coal power plant with CCS - Retrofit post-combustion
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | -60 | -60 | -60 |  |  |  |  | A | 1
Generating capacity for total power plant | MW_e | -60 | -60 | -60 |  |  |  |  | A | 1
Electricity efficiency, net, name plate | % | -7 | -7 | -7 | [5 empty] | 1
Electricity efficiency, net, annual average | % | -8 | -8 | -8 | [5 empty] | 1
Forced outage | % | 7 | 7 | 7
Planned outage | weeks per year
Technical lifetime | years
Construction time | years
CO2 emission reduction | % | -89 | -90 | -90 |  |  | -90 | -99 | B | 1
Space requirement | 1000 m2/MW_e
Ramping configurations
Ramping | % per minute | 4 | 4 | 4 |  |  |  |  | C | 7
Minimum load | % of full load | 30 | 30 | 30 |  |  |  |  | D | 7
Warm start-up time | hours | 4 | 4 | 4 |  |  |  |  | E | 8
Cold start-up time | hours | 12 | 12 | 12 |  |  |  |  | E | 8
Environment
PM 2.5 | g/Nm3 | 81 | 81 | 81 | [5 empty] | 3, 7
SO2 (degree of desulphuring,) | % | 97 | 97 | 97 | [5 empty] | 3, 7
NOX | g/GJ fuel | 152 | 150 | 38 | [5 empty] | 3, 7
CH4 | g/GJ fuel
N2O | g/GJ fuel
Economic data (in USD2025)
Nominal investment | M$/MW_e | 3.61 | 3.32 | 2.63 | 2.07 | 4.05 | 1.51 | 3.25 | F | 2, 5, 9, 10, 11, 12
- of which equipment | % | 30 | 30 | 30 | 25 | 50 | 25 | 50 |  | 1
- of which installation | % | 70 | 70 | 70 | 50 | 75 | 50 | 75 |  | 1
Fixed O&M | $/MW_e/year | 54157 | 52414 | 50920 | 16807 | 64739 | 16807 | 64739 | F | 1, 7, 9
Variable O&M | $/MWh | 4.01 | 3.9 | 3.77 | 3.24 | 10.61 | 3.04 | 9.98 | F | 1, 5, 9
Technology specific data
Water consumption | L/MWh | 3200 | 3200 | 3200 | - | - | - | - | G | 13, 14
Notes:
A | The difference in output power represents the additional power required by the auxiliary equipment (with CCS, ~15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | Compression, transport and storage are not included in the figures.
G | Assuming a cooling tower is used.
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | EIA, 2016, Capital Cost Estimates for Utility Scale Electricity Generating Plants
6 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermittent renewable energy sources
7 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2024
8 | IEAGHG, Operating Flexibility of Power Plants with CCS
9 | NREL ATB 2020
10 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020
11 | ADB. Prospect for carbon capture and storage in Southeast Asia. Asian Development Bank, http://www.adb.org/publications/prospects-carbon-capture-and-storage-southeast-asia. 2012
12 | MOIT, ADB, GCCSI, Determining the potential for carbon capture and storage in Southeast Asia, Vietnam Country Report, 2012
13 | International Energy Agency, 2016 - Water Energy Nexus
14 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies

## Natural gas CCS
Natural Gas Combined Cycle with CCS - Retrofit post-combustion
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | -40 | -40 | -40 |  |  |  |  | A | 1
Generating capacity for total power plant | MW_e | -40 | -40 | -40 |  |  |  |  | A | 1
Electricity efficiency, net, name plate | % | -7 | -7 | -7 | [5 empty] | 1
Electricity efficiency, net, annual average | % | -8 | -8 | -8 | [5 empty] | 1
Forced outage | % | 5 | 5 | 5
Planned outage | weeks per year
Technical lifetime | years | -
Construction time | years
CO2 emission reduction | % | -87 | -90 | -90 |  |  | -90 | -99 | B | 1
Space requirement | 1000 m2/MW_e
Ramping configurations
Ramping | % per minute | 20 | 20 | 20 |  |  |  |  | C | 6
Minimum load | % of full load | 45 | 45 | 45 |  |  |  |  | D | 6
Warm start-up time | hours | 2,0 | 2,0 | 2,0 |  |  |  |  | E | 4
Cold start-up time | hours | 4,0 | 4,0 | 4,0 |  |  |  |  | E | 4
Environment
PM 2.5 | g/Nm3 | 30 | 30 | 30 | [5 empty] | 3, 6
SO2 (degree of desulphuring,) | % | 99 | 99 | 99 | [5 empty] | 3, 6
NOX | g/GJ fuel | 78 | 60 | 20 | [5 empty] | 3, 6
CH4 | g/GJ fuel | - | - | -
N2O | g/GJ fuel | - | - | -
Economic data (in USD2025)
Nominal investment | M$/MW_e | 1.86 | 1.57 | 1.21 | 1.1 | 3.33 | 0.78 | 2.53 | F | 1, 7, 8, 9, 10
- of which equipment | % | 40 | 40 | 40 | 30 | 60 | 30 | 60 |  | 1
- of which installation | % | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 1
Fixed O&M | $/MWe/year | 11703 | 11205 | 10956 | 9088 | 18177 | 8590 | 18177 | F | 1, 7, 8
Variable O&M | $/MWh | 1.55 | 1.5 | 1.46 | 0.78 | 5.18 | 0.78 | 5.18 | F | 1, 7, 8
Technology specific data
Water consumption | L/MWh | 1500 | 1500 | 1500 | - | - | - | - | G | 11, 12
Notes:
A | The difference in output power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | Compression, transport and storage are not included in the figures.
G | Assuming a cooling tower is used.
References
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., Carbon Dioxide Capture and Air Quality, 2011
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermittent renewable energy sources
6 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2024
7 | NREL ATB, 2020
8 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020
9 | ADB. Prospect for carbon capture and storage in Southeast Asia. Asian Development Bank, http://www.adb.org/publications/prospects-carbon-capture-and-storage-southeast-asia. 2012
10 | MOIT, ADB, GCCSI, Determining the potential for carbon capture and storage in Southeast Asia, Viet Nam Country Report, 2012
11 | "National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies"
12 | International Energy Agency, 2016 - Water Energy Nexus

## Biomass cogeneration
Biomass-fired cogeneration
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 25 | 25 | 25 | 4 | 200 | 4 | 200 |  | 1, 5, 12
Generating capacity for total power plant | MW_e | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1, 5
Electricity efficiency, net, name plate | % | 27 | 27 | 27 | 20 | 30 | 20 | 30 |  | 1, 3, 7
Electricity efficiency, net, annual average | % | 26 | 26 | 26 | 20 | 30 | 20 | 30 | D | 1, 3, 7
Total efficiency, net, name plate | % | 85 | 85 | 85 | 80 | 90 | 80 | 90 |  | 11
Total efficiency, net, annual average | % | 84 | 84 | 84 | 80 | 90 | 80 | 90 |  | 11
Forced outage | % | 7 | 7 | 7 | 5 | 9 | 5 | 9 | A | 1
Planned outage | weeks per year | 26 | 26 | 26 | 24 | 28 | 24 | 28 | C | 1
Technical lifetime | years | 25 | 25 | 25 | 19 | 31 | 19 | 31 | A | 8, 7
Construction time | years | 2 | 2 | 2 | 2 | 3 | 2 | 3 | A | 7
Space requirement | 1000 m2/MW_e | 35 | 35 | 35 | 26 | 44 | 26 | 44 | A | 1, 9
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | -
Ramping configurations
Ramping | % per minute | 10 | 10 | 10 | [5 empty] | 3
Minimum load | % of full load | 30 | 30 | 30 | [5 empty] | 3
Warm start-up time | hours | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Cold start-up time | hours | 10 | 10 | 10 | [5 empty] | 3
Environment
PM 2.5 | g/Nm3 | 12.5 | 12.5 | 12.5 | [5 empty] | 3
SO2 (degree of desulphuring,) | % | 0 | 0 | 0 | [5 empty] | 3
NOX | g/GJ fuel | 125 | 125 | 125 | [5 empty] | 3
Economic data (in USD2025)
Nominal investment | M$/MW_e | 2.2 | 2 | 1.8 | 1.7 | 3.1 | 1.3 | 2.2 | B | 4, 5, 6, 7, 8, 10
- of which equipment | % | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1, 2
- of which installation | % | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1, 2
Fixed O&M | $/MWe/year | 61627 | 56647 | 49301 | 46220 | 83196 | 36976 | 61627 | A | 4, 5, 8, 10
Variable O&M | $/MWh | 3.9 | 3.6 | 3.2 | 3 | 5.3 | 2.4 | 3.9 | A | 5, 10
Start-up costs | $/MW_e/start-up
Technology specific data
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | Lower and upper uncertainties are for 2025 -25% (lower) and +35% (higher) and for 2050 -/+25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | Sugar production season is approximately half a year.
D | Power efficiency is reduced by 5 %-points compared to condensing operation to reflect steam extraction at higher temperature for process heat.
References
1 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024
2 | ASEAN Centre of Energy, "Levelized cost of electricity generation of selected renewable energy technologies in the ASEAN member states", 2016
3 | Danish Energy Agency and COWI, "Technology catalogue for biomass to energy", 2017
4 | IRENA, "Renewable power generation cost in 2014", 2015
5 | IFC and BMF, "Converting biomass to energy - A guide for developers and investors", 2017
6 | OJK, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, 2014
7 | IEA-ETSAP and IRENA, "Biomass for Heat and Power, Technology Brief", 2015
8 | PKPPIM, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy, Ministry of Finance Indonesia, 2014
9 | India Central Electricity Authority, "Report on the Land Requirement of Thermal Power Stations", 2007
10 | Learning curve approach for the development of financial parameters
11 | Siemens, "The powerful potential of sugarcane", 2018

## Cement CHP
CHP in a cement factory
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 8 | 8 | 8 | 2 | 20 | 2 | 20 |  | 1, 2, 3
Generating capacity for total power plant | MW_e
Electricity efficiency, net, name plate | % | 18 | 18 | 18 | 15 | 25 | 15 | 25 |  | 3
Electricity efficiency, net, annual average | %
Forced outage | %
Planned outage | weeks per year
Technical lifetime | years
Construction time | years
Space requirement | 1000 m2/MW_e
Additional data for non-thermal plants
Capacity factor, theoretical | %
Capacity factor, incl. outages | %
Ramping configurations
Ramping | % per minute
Minimum load | % of full load
Warm start-up time | hours
Cold start-up time | hours
Environment
PM 2.5 | g/Nm3
SO2 (degree of desulphuring,) | %
NOX | g/GJ fuel
Economic data (in USD2025)
Nominal investment | M$/MW_e | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 |  | 4
- of which equipment | % | 85 | 85 | 85 | 85 | 85 | 85 | 85 | A
- of which installation | % | 15 | 15 | 15 | 15 | 15 | 15 | 15 | A
Fixed O&M | $/MWe/year
Variable O&M | $/MWh | 15.56 | 15.56 | 15.56 | 6.22 | 24.9 | 6.22 | 24.9 |  | 2
Start-up costs | $/MW_e/start-up
Technology specific data
Water consumption | L/MWh | - | - | - | - | - | - | -
Notes:
A | Estimated.
References
1 | Khurana, S., Banerjee, J., & Gaitonde, U. (2006). Energy balance and cogeneration for a cement plant. Appl. Therm. Eng., 2479-2489
2 | Irungu, S. N., & Muchiri, P. &. (2017). The generation of power from a cement kiln waste gases: a case study of a plant in Kenya. Energy Science & Engineering, 90-99
3 | Paredes-Sánchez, J. P. (2015). Using waste energy from the Organic Rankine Cycle cogeneration in the Portland cement industry. DYNA, 15-20
4 | Institute for Industrial Productivity. (2014). Waste Heat Recovery for the Cement Sector: Market and Supplier Analysis

## Small hydro
Hydro power plant - small system
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 10 | 10 | 10 | 10 | 1 | 30 | 1 | 30
Generating capacity for total power plant | MW_e | 20 | 20 | 20 | 20 | 1 | 30 | 1 | 30
Electrical efficiency, net, name plate | % | 95 | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 5
Electrical efficiency, net, annual average | % | 95 | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 5
Forced outage | % | 4 | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 5
Planned outage | % | 10.6 | 10.6 | 10.6 | 10.6 | 5.8 | 19.2 | 5.8 | 19.2 |  | 7
Self-consumption | % | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 1.3 | 0.4 | 1.3
Technical lifetime | years | 50 | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 5
Construction time | years | 3 | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 5
Space requirement | 1000_m2/MW_e | 32 | 32 | 32 | 32 | 11 | 69 | 11 | 69
Additional data for non-thermal plants
Capacity factor, theoretical | % | 59 | 59 | 59 | 59 | 57 | 70 | 57 | 70
Capacity factor, incl. outages | % | 50 | 50 | 50 | 50 | 40 | 65 | 40 | 65
Ramping ability
Ramping | % of full load/minute | 50 | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 6
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6
Warm start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 6
Cold start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 6
Minimum Up time | hours | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1
Minimum Down time | hours | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 1.8 | 1.8 | 1.79 | 1.79 | 0.8 | 4.4 | 0.79 | 4.36 | A
- of which equipment | % | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 1
- of which installation and other costs | % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | B | 1
- of which equipment | MUSD/MW_e | 0.72 | 0.72 | 0.72 | 0.71 | - | - | - | - | A
- of which installation and other costs | MUSD/MW_e | 1.08 | 1.08 | 1.07 | 1.07 | - | - | - | - | A
Fixed O&M | USD/MW_e/year | 39600 | 39503 | 39365 | 39280 | 16000 | 110000 | 15871 | 109110 | A, C
Variable O&M | USD/MWh | 0.5 | 0.5 | 0.5 | 0.5 | 0.38 | 0.63 | 0.37 | 0.62 | D
Start-up costs | USD/MW_e/start-up
Technology specific data
Water Consumption | L/MWh | ~1000 | ~1000 | ~1000 | ~1000 | - | - | - | - | E | 2, 3, 4
Notes:
A | Costs are very site sensitive. Costs are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2025, with Stated Policies for the central values.
B | For hydropower plants the civil works and earthworks often make up a significant share of the costs which are included as installation as described in the overall methodology for the Technology Catalogue.
C | O&M corresponding to 2.2% of CAPEX/year according to IEA with an uncertainty range of 2% to 2.5% for large-scale plants according to IRENA.
D | Uncertainty (Upper/Lower) is estimated as +/- 25%.
E | The water consumption can vary a lot. It is based on evaporation losses which depend on the reservoir size. If there is no reservoir, the water consumption can be very low.
References
1 | IRENA, 2025 - Renewable Power Generation Costs in 2024
2 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
3 | SINTEF, 2016 - The life-cycle water footprint of two hydropower projects in Norway
4 | Argonne national laboratory, 2018 - Regional Water Consumption for Hydro and Thermal Electricity Generation in the United States
5 | Stepan, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”, 2011
6 | Eurelectric, "Hydropower - Supporting a power system in transition", 2015
7 | Based on projects in Vietnam

## Large hydro
Hydro power plant - large system
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 150 | 150 | 150 | 150 | 30 | 400 | 0 | 0 |  | 5, 6, 7
Generating capacity for total power plant | MW_e | 150 | 150 | 150 | 150 | 30 | 2000 | 30 | 2000 |  | 5, 6, 7
Electrical efficiency, net, name plate | % | 95 | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
Electrical efficiency, net, annual average | % | 95 | 95 | 95 | 95 | 85 | 97 | 85 | 97 |  | 8
Forced outage | % | 4 | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 5
Planned outage | % | 11.5 | 11.5 | 11.5 | 11.5 | 5.8 | 19.2 | 5.8 | 19.2 |  | 9
Self-consumption | % | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 1.5 | 0.5 | 1.5
Technical lifetime | years | 50 | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 9, 5
Construction time | years | 4 | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 9, 5
Space requirement | 1000_m2/MW_e | 100 | 100 | 100 | 100 | 47 | 143 | 47 | 143
Additional data for non-thermal plants
Capacity factor, theoretical | % | 53 | 53 | 53 | 53 | 49 | 60 | 49 | 60
Capacity factor, incl. outages | % | 45 | 45 | 45 | 45 | 35 | 55 | 35 | 55
Ramping ability
Ramping | % of full load/minute | 50 | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 10
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10
Warm start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 10
Cold start-up time | hours | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 10
Minimum Up time | hours | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1
Minimum Down time | hours | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 2 | 2 | 1.99 | 1.98 | 0.75 | 8.8 | 0.74 | 8.73 | A
- of which equipment | % | 30 | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
- of which installation and other costs | % | 70 | 70 | 70 | 70 | 50 | 80 | 50 | 80 | B | 1
- of which equipment | MUSD/MW_e | 0.6 | 0.6 | 0.6 | 0.6 | - | - | - | - | A
- of which installation and other costs | MUSD/MW_e | 1.4 | 1.4 | 1.39 | 1.39 | - | - | - | - | A
Fixed O&M | USD/MW_e/year | 44000 | 43893 | 43739 | 43644 | 15000 | 220000 | 14879 | 218220 | A, C
Variable O&M | USD/MWh | 0.75 | 0.75 | 0.75 | 0.74 | 0.56 | 0.94 | 0.56 | 0.93 | D
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 19000 | 19000 | 19000 | 19000 | - | - | - | - | E | 2, 3, 4
Notes:
A | Costs are projected with a learning rate approach assuming a 1% learning rate for based on IEA's assumptions in their Global Energy and Climate Model, including capacity projections of the IEA's World Energy Outlook 2025, with Stated Policies for the central values.
B | For large hydropower plants the civil works and earthworks to establish tunnelling and dams are often the biggest share of the costs (around 50% according to IEA). These costs are included as installation costs as described in the overall methodology for the Technology Catalogue.
C | O&M corresponding to 2.2% of CAPEX/year according to IEA with an uncertainty range of 2% to 2.5% for large-scale plants according to IRENA.
D | Uncertainty (Upper/Lower) is estimated as +/- 25%.
E | The water consumption can vary a lot. It is based on evaporation losses which depend on the reservoir size. If there is no reservoir, the water consumption can be very low. On the contrary, if the reservoir is big, the evaporation losses can be substantial.
References
1 | IRENA, 2025 - Renewable Power Generation Costs in 2024
2 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity
Generating Technologies
3 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
4 | Argonne national laboratory, 2018 - Regional Water Consumption for Hydro and Thermal Electricity Generation in the United States
5 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024.
6 | Prayogo, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar", 2003.
7 | General Electric, www.gerenewableenergy.com, Accessed: 20th July 2017.
8 | Stepan, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”, 2011.
9 | Based on existing projects in Vietnam
10 | Eurelectric, "Hydropower - Supporting a power system in transition", 2015.

## Rooftop solar
Rooftop solar
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | kW_e
Generating capacity for a typical power plant | kW_e | 10 | 10 | 10 | 10 | 2 | 20 | 2 | 20 |  | 1
Forced outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Planned outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Technical lifetime | years | 30 | 32 | 35 | 40 | 25 | 35 | 35 | 45 |  | 2, 3
Construction time | years | 0.08 | 0.08 | 0.08 | 0.08 | 0.01 | 0.13 | 0.01 | 0.13 |  | 1
Space requirement | 1000 m2/MW_p | 6.5 | 6.1 | 5.7 | 5.4 | 4.9 | 8.1 | 4 | 6.7 |  | 1, 2, 3
Additional data for non-thermal plants
Capacity factor, theoretical | % | 17.2 | 17.7 | 18.1 | 18.7 | 11 | 24 | 12 | 26.1 | A
Capacity factor, incl. outages | % | 17.2 | 17.7 | 18.1 | 18.7 | 11 | 24 | 12 | 26.1 | A
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 0.85 | 0.61 | 0.47 | 0.42 | 0.74 | 0.99 | 0.36 | 0.44 | B, C | 1
- of which equipment | % | 48 | 47 | 46 | 45 | - | - | - | - |  | 1, 2, 4, 5
- of which installation and other costs | % | 52 | 53 | 54 | 55 | - | - | - | - |  | 1, 2, 4, 5
PV module cost | MUSD/MW_e | 0.28 | 0.19 | 0.13 | 0.12 | 0.24 | 0.33 | 0.1 | 0.13 | C | 1, 2, 4, 5
PV inverter cost | MUSD/MW_e | 0.13 | 0.1 | 0.08 | 0.07 | 0.12 | 0.15 | 0.06 | 0.07 | C | 1, 2, 4, 5
Balance Of Plant cost | MUSD/MW_e | 0.23 | 0.17 | 0.13 | 0.12 | 0.2 | 0.27 | 0.11 | 0.13 | C | 1, 2, 4, 5
Installation cost | MUSD/MW_e | 0.21 | 0.16 | 0.12 | 0.11 | 0.18 | 0.24 | 0.1 | 0.12 | C | 1, 2, 4, 5
Fixed O&M | USD/MW_e/year | 12800 | 11105 | 9875 | 9425 | 12043 | 14428 | 8868 | 9658 | C | 1, 6
Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Full load hours | kWh/kW | 1511 | 1547 | 1584 | 1638 | 966 | 2105 | 1047 | 2283 | A, D
Peak full load hours | kWh/kW_p | 1314 | 1345 | 1377 | 1425 | 920 | 1754 | 998 | 1902 | A, D
Global horizontal irradiance | kWh/m2/y | 1550 | 1550 | 1550 | 1550 | 1150 | 2000 | 1150 | 2000 | E | 7
DC/AC sizing factor | W_p/W | 1.15 | 1.15 | 1.15 | 1.15 | 1.05 | 1.2 | 1.05 | 1.2 | F | 1, 3
Transposition Factor |  | 1.02 | 1.02 | 1.02 | 1.02 | 1 | 1.02 | 1 | 1.02 | G | 7
Performance ratio |  | 0.83 | 0.85 | 0.87 | 0.9 | 0.8 | 0.86 | 0.87 | 0.93 | H | 1, 2, 3
PV module conversion efficiency | % | 21.5 | 23 | 24.5 | 26 | 20 | 23 | 24.2 | 27.8 | I | 1, 3
Inverter lifetime | years | 15 | 15 | 15 | 15 | 12.5 | 16 | 12.5 | 16 |  | 1
Average annual degradation of FLH | % | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.8 | 0.3 | 0.8 | J | 2
Water consumption |  | < 100 | < 100 | < 100 | < 100 | - | - | - | - | K | 8, 9, 10, 11
Economic data - per DC peak cap.
Nominal investment | MUSD/MW_p(DC) | 0.74 | 0.53 | 0.41 | 0.36 | 0.7 | 0.82 | 0.35 | 0.37
PV module cost | MUSD/MW_p(DC) | 0.24 | 0.16 | 0.12 | 0.1 | 0.22 | 0.27 | 0.09 | 0.11
PV inverter cost | MUSD/MW_p(DC) | 0.11 | 0.09 | 0.07 | 0.06 | 0.11 | 0.13 | 0.06 | 0.06
Balance Of Plant cost | MUSD/MW_p(DC) | 0.2 | 0.15 | 0.12 | 0.1 | 0.19 | 0.22 | 0.1 | 0.11
Installation cost | MUSD/MW_p(DC) | 0.18 | 0.14 | 0.11 | 0.1 | 0.18 | 0.2 | 0.09 | 0.1
Fixed O&M | USD/MW_p(DC)/year | 11130 | 9656 | 8587 | 8195 | 11470 | 12023 | 8445 | 8048
Variable O&M | USD/MWh_p(DC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
A | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1550 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
B | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | Costs are projected with a learning rate approach assuming a 25.7% learning rate for modules based on Fraunhofer [5], 19% learning rate for inverters based on the Danish Technology Catalogue for Generation of Electricity and District Heating [2], and 20% as per other components based on IEA, and 10% for O&M, including capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
D | The number of full load hours is calculated based on other values in the table. The formula is: Full load hours = DC/AC sizing factor * peak full load hours. The formula used to calculate Peak full load hours is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
E | The central value is the average annual solar irradiance received on a horizontal surface in Vietnam. Hanoi receives 1330 kWh/m2/year and Ho Chi Mich City receives 1800 kWh/m2/year. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Vietnam.
F | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
G | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from south. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF.
H | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
I | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
J | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors.
K | Solar PVs do not need water for cooling, however water can be used for cleaning.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
3 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
4 | IRENA, 2024 - Renewable Power Generation Costs in 2024
5 | Fraunhofer, 2025, Photovoltaics Report
6 | Stakeholder dialogue
7 | World Bank, Global Solar Atlas
8 | International Energy Agency, 2016 - Water Energy Nexus
9 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
10 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains
11 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Utility solar
Utility Scale Solar PV (fixed)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e
Generating capacity for a typical power plant | MW_e | 100 | 100 | 100 | 100 | 70 | 200 | 70 | 200 |  | 1
Forced outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Planned outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Technical lifetime | years | 30 | 32 | 35 | 40 | 25 | 35 | 35 | 45 |  | 2, 3
Construction time | years | 0.7 | 0.7 | 0.5 | 0.5 | 0.3 | 1 | 0.2 | 0.7 |  | 1
Space requirement | 1000 m2/MW_p | 11 | 10.3 | 9.7 | 9.1 | 9 | 12 | 7.4 | 9.9 |  | 1, 2, 3
Additional data for non-thermal plants
Capacity factor, theoretical | % | 19.5 | 20 | 20.4 | 21.1 | 11.7 | 26 | 12.7 | 28.2 | A
Capacity factor, incl. outages | % | 19.5 | 20 | 20.4 | 21.1 | 11.7 | 26 | 12.7 | 28.2 | A
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 0.73 | 0.52 | 0.4 | 0.36 | 0.63 | 0.85 | 0.31 | 0.38 | B, C | 1
- of which equipment | % | 44 | 42 | 41 | 40 | - | - | - | - |  | 1, 2, 4, 5
- of which installation and other costs | % | 56 | 58 | 59 | 60 | - | - | - | - |  | 1, 2, 4, 5
PV module cost | MUSD/MW_e | 0.25 | 0.17 | 0.12 | 0.11 | 0.21 | 0.29 | 0.09 | 0.11 | C | 1, 2, 4, 5
PV inverter cost | MUSD/MW_e | 0.07 | 0.05 | 0.04 | 0.04 | 0.06 | 0.08 | 0.03 | 0.04 | C | 1, 2, 4, 5
Balance Of Plant cost | MUSD/MW_e | 0.24 | 0.18 | 0.14 | 0.13 | 0.21 | 0.28 | 0.11 | 0.13 | C | 1, 2, 4, 5
Installation cost | MUSD/MW_e | 0.17 | 0.13 | 0.1 | 0.09 | 0.15 | 0.2 | 0.08 | 0.09 | C | 1, 2, 4, 5
Fixed O&M | USD/MW_e/year | 10000 | 8676 | 7715 | 7363 | 9409 | 11272 | 6928 | 7545 | C | 1, 6
Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Full load hours | kWh/kW | 1708 | 1749 | 1790 | 1852 | 1025 | 2281 | 1111 | 2473 | A, D
Peak full load hours | kWh/kW_p | 1314 | 1345 | 1377 | 1425 | 932 | 1754 | 1010 | 1902 | A, D
Global horizontal irradiance | kWh/m2/y | 1550 | 1550 | 1550 | 1550 | 1150 | 2000 | 1150 | 2000 | E | 7
DC/AC sizing factor | W_p/W | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.3 | 1.1 | 1.3 | F | 1, 3
Transposition Factor |  | 1.02 | 1.02 | 1.02 | 1.02 | 1 | 1.02 | 1 | 1.02 | G | 7
Performance ratio |  | 0.83 | 0.85 | 0.87 | 0.9 | 0.81 | 0.86 | 0.88 | 0.93 | H | 1, 2, 3
PV module conversion efficiency | % | 21.5 | 23 | 24.5 | 26 | 20 | 23 | 24.2 | 27.8 |  | 1, 3
Inverter lifetime | years | 15 | 15 | 15 | 15 | 12.5 | 16 | 12.5 | 16 |  | 1
Average annual degradation of FLH | % | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 | J | 1
Water consumption |  | < 100 | < 100 | < 100 | < 100 | - | - | - | - | K | 8, 9, 10, 11
Economic data - per DC peak cap.
Nominal investment | MUSD/MW_p(DC) | 0.56 | 0.4 | 0.31 | 0.28 | 0.58 | 0.65 | 0.28 | 0.29
PV module cost | MUSD/MW_p(DC) | 0.19 | 0.13 | 0.09 | 0.08 | 0.19 | 0.23 | 0.08 | 0.09
PV inverter cost | MUSD/MW_p(DC) | 0.05 | 0.04 | 0.03 | 0.03 | 0.06 | 0.06 | 0.03 | 0.03
Balance Of Plant cost | MUSD/MW_p(DC) | 0.18 | 0.14 | 0.11 | 0.1 | 0.19 | 0.21 | 0.1 | 0.1
Installation cost | MUSD/MW_p(DC) | 0.13 | 0.1 | 0.08 | 0.07 | 0.14 | 0.15 | 0.07 | 0.07
Fixed O&M | USD/MW_p(DC)/year | 7692 | 6674 | 5935 | 5664 | 8554 | 8671 | 6298 | 5804
Variable O&M | USD/MWh_p(DC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
A | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1550 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
B | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | Costs are projected with a learning rate approach assuming a 25.7% learning rate for modules based on Fraunhofer [5], 19% learning rate for inverters based on the Danish Technology Catalogue for Generation of Electricity and District Heating [2], and 20% as per other components based on IEA, and 10% for O&M, including capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
D | The number of full load hours is calculated based on other values in the table. The formula is: Full load hours = DC/AC sizing factor * peak full load hours. The formula used to calculate Peak full load hours is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
E | The central value is the average annual solar irradiance received on a horizontal surface in Vietnam. Hanoi receives 1330 kWh/m2/year and Ho Chi Mich City receives 1800 kWh/m2/year. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Vietnam.
F | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
G | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from south. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF.
H | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
I | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
J | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors.
K | Solar PVs do not need water for cooling, however water can be used for cleaning.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
3 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
4 | IRENA, 2024 - Renewable Power Generation Costs in 2024
5 | Fraunhofer, 2025, Photovoltaics Report
6 | Stakeholder dialogue
7 | World Bank, Global Solar Atlas
8 | International Energy Agency, 2016 - Water Energy Nexus
9 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
10 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains
11 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Floating solar
Floating PV
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e
Generating capacity for a typical power plant | MW_e | 40 | 70 | 80 | 100 | [5 empty] | 1
Forced outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Planned outage | % | 0 | 0 | 0 | 0 | - | - | - | -
Technical lifetime | years | 30 | 32 | 35 | 40 | 25 | 35 | 35 | 45 |  | 2, 3
Construction time | years | 0.7 | 0.7 | 0.5 | 0.5 | 0.3 | 1 | 0.2 | 0.7 |  | 1, 2, 3
Space requirement | 1000 m2/MW_p | 10 | 9.3 | 8.8 | 8.3 | 8.5 | 12 | 7 | 9.9 |  | 1, 2, 3
Additional data for non-thermal plants
Capacity factor, theoretical | % | 20.5 | 21 | 21.5 | 22.2 | 12.3 | 27.3 | 13.3 | 29.6 | A
Capacity factor, incl. outages | % | 20.5 | 21 | 21.5 | 22.2 | 12.3 | 27.3 | 13.3 | 29.6 | A
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 1.04 | 0.75 | 0.58 | 0.52 | 0.95 | 1.65 | 0.25 | 0.65 | B, C, D | 1
- of which equipment | % | 35 | 33.6 | 32.3 | 31.8 | - | - | - | - |  | 1, 2, 4, 5
- of which installation and other costs | % | 65 | 66.4 | 67.7 | 68.2 | - | - | - | - |  | 1, 2, 4, 5
PV module cost | MUSD/MW_e | 0.29 | 0.19 | 0.14 | 0.12 | 0.24 | 0.45 | 0.1 | 0.13 | D | 1, 2, 4, 5
PV inverter cost | MUSD/MW_e | 0.08 | 0.06 | 0.05 | 0.04 | 0.07 | 0.13 | 0.04 | 0.05 | D | 1, 2, 4, 5
Balance Of Plant cost | MUSD/MW_e | 0.4 | 0.29 | 0.23 | 0.21 | 0.35 | 0.63 | 0.18 | 0.22 | D | 1, 2, 4, 5
Installation cost | MUSD/MW_e | 0.28 | 0.21 | 0.16 | 0.15 | 0.25 | 0.44 | 0.13 | 0.15 | D | 1, 2, 4, 5
Fixed O&M | USD/MW_e/year | 15000 | 13013 | 11573 | 11045 | 14113 | 16908 | 10392 | 11317 | D | 1, 6
Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Full load hours | kWh/kW | 1793 | 1836 | 1880 | 1944 | 1076 | 2395 | 1167 | 2597 | A, E
Peak full load hours | kWh/kW_p | 1379 | 1413 | 1446 | 1496 | 978 | 1842 | 1061 | 1997 | A, E
Global horizontal irradiance | kWh/m2/y | 1550 | 1550 | 1550 | 1550 | 1150 | 2000 | 1150 | 2000 | F | 7
DC/AC sizing factor | W_p/W | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.3 | 1.1 | 1.3 | G | 1, 3
Transposition Factor |  | 1.02 | 1.02 | 1.02 | 1.02 | 1 | 1.02 | 1 | 1.02 | H | 7
Performance ratio |  | 0.87 | 0.89 | 0.91 | 0.95 | 0.85 | 0.9 | 0.92 | 0.98 | I, J | 1, 2, 3
PV module conversion efficiency | % | 21.5 | 23 | 24.5 | 26 | 20 | 23 | 24.2 | 27.8 | K | 1, 3
Inverter lifetime | years | 15 | 15 | 15 | 15 | 12.5 | 16 | 12.5 | 16 |  | 1
Average annual degradation of FLH | % | 2 | 2 | 2 | 2 | 0.5 | 3 | 0.5 | 3 | L | 2
Water consumption |  | < 100 | < 100 | < 100 | < 100 | - | - | - | -
Economic data - per DC peak cap.
Nominal investment | MUSD/MW_p(DC) | 0.8 | 0.58 | 0.44 | 0.4 | 0.86 | 1.27 | 0.23 | 0.5
PV module cost | MUSD/MW_p(DC) | 0.22 | 0.15 | 0.11 | 0.09 | 0.22 | 0.35 | 0.09 | 0.1
PV inverter cost | MUSD/MW_p(DC) | 0.06 | 0.05 | 0.04 | 0.03 | 0.06 | 0.1 | 0.04 | 0.04
Balance Of Plant cost | MUSD/MW_p(DC) | 0.3 | 0.23 | 0.18 | 0.16 | 0.32 | 0.48 | 0.17 | 0.17
Installation cost | MUSD/MW_p(DC) | 0.22 | 0.16 | 0.12 | 0.11 | 0.22 | 0.34 | 0.12 | 0.12
Fixed O&M | USD/MW_p(DC)/year | 11538 | 10010 | 8902 | 8496 | 12830 | 13006 | 9447 | 8706
Variable O&M | USD/MWh_p(DC) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
A | The capacity factor or full load hours depend greatly on the global horizontal irradiance at the specific plant site. For sites significantly different from the 1550 kWh/m2/year solar irradiation mentioned here, the capacity factors should be adjusted accordingly.
B | Investment cost includes the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | Overall cost estimation based on utility-scale datasheet, considering that floating PV plants are expected to be approx. 25% more expensive than ground-mounted utility-scale plants, with the mark-up apparent in installation and other cost incl. balance of plant.
D | Costs are projected with a learning rate approach assuming a 25.7% learning rate for modules based on Fraunhofer [5], 19% learning rate for inverters based on the Danish Technology Catalogue for Generation of Electricity and District Heating [2], and 20% as per other components based on IEA, and 10% for O&M, including capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
E | The number of full load hours is calculated based on other values in the table. The formula is: Full load hours = DC/AC sizing factor * peak full load hours. The formula used to calculate Peak full load hours is: Peak full load hours = Global horizontal irradiance * transposition factor * performance ratio.
F | The central value is the average annual solar irradiance received on a horizontal surface in Vietnam. Hanoi receives 1330 kWh/m2/year and Ho Chi Mich City receives 1800 kWh/m2/year. Minimum and maximum value correspond to The Global Solar Atlas's s Global Horizontal Irradiation distribution for Vietnam.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from south. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifier, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The surrounding water can have an effect on the performance ratio in terms of its cooling and reflective properties, which typically lies 5% above comparable ground-mounted onshore PV plants.
K | The efficiency is a market average of commercial modules. Modules with above 21 % efficiency are commercially available. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon HJT n-type mono-Si cells which both have higher efficiencies.
L | Annual degradation of full load hours is not included in the above figures of full-load hours and capacity factors.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
3 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
4 | IRENA, 2024 - Renewable Power Generation Costs in 2024
5 | Fraunhofer, 2025, Photovoltaics Report
6 | Stakeholder dialogue
7 | World Bank, Global Solar Atlas
8 | International Energy Agency, 2016 - Water Energy Nexus
9 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
10 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains
11 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Onshore wind-High
Onshore Wind – High turbine
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 5 | 6 | 6.2 | 6.5 | 3.5 | 7 | 5.5 | 9 |  | 1
Generating capacity for a typical power plant | MW_e | 100 | 100 | 100 | 100 | 30 | 300 | 30 | 300 |  | 1, 2
Forced outage | % | 2.5 | 2 | 2 | 2 | - | - | - | - |  | 1, 2, 3
Planned outage | % | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - |  | 1, 2, 3
Technical lifetime | years | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 |  | 1, 2, 3
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 1, 2, 3
Space requirement | 1000 m2/MW_e | 14 | 14 | 14 | 14 | - | - | - | - |  | 2, 4
Additional data for non-thermal plants
Capacity factor, theoretical | % | 35 | 35.3 | 36.3 | 36.9 | 26.2 | 43.7 | 27.6 | 46.1 | A
Capacity factor, incl. outages | % | 34 | 34.5 | 35.5 | 36 | 25.5 | 42.5 | 27 | 45 | A | 1, 2
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 1.37 | 1.32 | 1.28 | 1.26 | 1.16 | 1.78 | 1.07 | 1.64 | B, C, F | 1, 5, 6
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | - | D | 1, 2, 4
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | - | D | 1, 2, 4
- of which equipment | MUSD/MW_e | 0.89 | 0.86 | 0.83 | 0.82 | 0.76 | 1.16 | 0.66 | 1.08 | D | 1, 2, 4
- of which installation and other costs | MUSD/MW_e | 0.48 | 0.46 | 0.45 | 0.44 | 0.41 | 0.62 | 0.36 | 0.58 | D | 1, 2, 4
Fixed O&M | USD/MW_e/year | 34250 | 32787 | 31541 | 31075 | 29113 | 44525 | 26857 | 41075 | B, E | 1
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | E
Technology specific data
Average annual full-load hours | MWh_e/MW_e | 2978 | 3022 | 3110 | 3154 | 2234 | 3723 | 2365 | 3942 |  | 1
Hub Height | m | 130 | 130 | 140 | 150 | - | - | - | - |  | 1
Rotor Diameter | m | 145 | 160 | 165 | 180 | - | - | - | - |  | 1
Specific Power | W/m2 | 303 | 298 | 290 | 286 | - | - | - | - |  | 1, 3
Availability | % | 97.2 | 97.7 | 97.7 | 97.7 | - | - | - | -
Water consumption |  | 0 | 0 | 0 | 0 | - | - | - | - |  | 7, 8
Notes:
A | Lower and upper uncertainties are +/- 25%.
B | Costs are projected with a learning rate approach assuming a 5% learning rate based on [6], and 6 % learning rate for OPEX based on [3]. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Lower and upper uncertainties are -15% and +30%.
D | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project. Central value assumes a 65/35 distribution.
E | O&M corresponding to 2.5 % of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
F | This cost estimate represents a general standard onshore wind project in Vietnam. Depending on varying factors like region, terrain, grid connection, transport difficulty, etc. the cost can vary significantly.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
3 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
4 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
5 | Stakeholder dialogue
6 | IEA, 2025 - World Energy Outlook 2025
7 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
8 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains

## Onshore wind-Medium
Onshore Wind – Medium turbine
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 4.5 | 4.5 | 5 | 5.2 | 3.5 | 6 | 4 | 7 |  | 1
Generating capacity for a typical power plant | MW_e | 50 | 70 | 80 | 100 | 30 | 70 | 50 | 150 |  | 1, 2
Forced outage | % | 2.5 | 2 | 2 | 2 | - | - | - | - |  | 1, 2, 3
Planned outage | % | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - |  | 1, 2, 3
Technical lifetime | years | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 |  | 1, 2, 3
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 1, 2, 3
Space requirement | 1000 m2/MW_e | 14 | 14 | 14 | 14 | - | - | - | - |  | 2, 4
Additional data for non-thermal plants
Capacity factor, theoretical | % | 36 | 36.3 | 36.9 | 37.9 | 27 | 45 | 28.4 | 47.3 | A
Capacity factor, incl. outages | % | 35 | 35.5 | 36 | 37 | 26.3 | 43.8 | 27.8 | 46.3 | A | 1, 2
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 1.5 | 1.45 | 1.4 | 1.38 | 1.28 | 1.95 | 1.18 | 1.8 | B, C, F | 1, 5, 6
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | - | D | 1, 2, 4
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | - | D | 1, 2, 4
- of which equipment | MUSD/MW_e | 0.98 | 0.94 | 0.91 | 0.9 | 0.83 | 1.27 | 0.73 | 1.18 | D | 1, 2, 4
- of which installation and other costs | MUSD/MW_e | 0.53 | 0.51 | 0.49 | 0.48 | 0.45 | 0.68 | 0.39 | 0.63 | D | 1, 2, 4
Fixed O&M | USD/MW_e/year | 37500 | 35898 | 34534 | 34024 | 31875 | 48750 | 29405 | 44973 | B, E | 1
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | E
Technology specific data
Average annual full-load hours | MWh_e/MW_e | 3066 | 3110 | 3154 | 3241 | 2300 | 3833 | 2431 | 4052 |  | 1
Hub Height | meter | 130 | 140 | 160 | 170 | - | - | - | - |  | 1
Rotor Diameter | meter | 155 | 155 | 165 | 170 | - | - | - | - |  | 1
Specific Power | W/m2 | 238 | 238 | 234 | 229 | - | - | - | - |  | 1, 3
Availability | % | 97.2 | 97.7 | 97.7 | 97.7 | - | - | - | -
Water consumption |  | 0 | 0 | 0 | 0 | - | - | - | - |  | 7, 8
Notes:
A | Lower and upper uncertainties are +/- 25%.
B | Costs are projected with a learning rate approach assuming a 5% learning rate based on [6], and 6 % learning rate for OPEX based on [3]. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Lower and upper uncertainties are -15% and +30%.
D | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project. Central value assumes a 65/35 distribution.
E | O&M corresponding to 2.5 % of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
F | This cost estimate represents a general standard onshore wind project in Vietnam. Depending on varying factors like region, terrain, grid connection, transport difficulty, etc. the cost can vary significantly.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
3 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
4 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
5 | Stakeholder dialogue
6 | IEA, 2025 - World Energy Outlook 2025
7 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
8 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains

## Onshore wind-Low
Onshore Wind – Low turbine
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 3 | 3.5 | 4 | 4.5 | 2.5 | 5 | 4 | 6.5 |  | 1
Generating capacity for a typical power plant | MW_e | 50 | 70 | 80 | 100 | 30 | 70 | 50 | 150 |  | 1, 2
Forced outage | % | 2.5 | 2 | 2 | 2 | - | - | - | - |  | 1, 2, 3
Planned outage | % | 0.3 | 0.3 | 0.3 | 0.3 | - | - | - | - |  | 1, 2, 3
Technical lifetime | years | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 |  | 1, 2, 3
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 1, 2, 3
Space requirement | 1000 m2/MW_e | 14 | 14 | 14 | 14 | - | - | - | - |  | 2, 4
Additional data for non-thermal plants
Capacity factor, theoretical | % | 38.1 | 38.9 | 39.9 | 40.9 | 28.6 | 47.6 | 30.7 | 51.2 | A
Capacity factor, incl. outages | % | 37 | 38 | 39 | 40 | 27.8 | 46.3 | 30 | 50 | A | 1, 2
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 1.65 | 1.59 | 1.54 | 1.52 | 1.4 | 2.06 | 1.23 | 1.77 | B, C, F | 1, 5, 6
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | - | D | 1, 2, 4
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | - | D | 1, 2, 4
- of which equipment | MUSD/MW_e | 1.07 | 1.03 | 1 | 0.99 | 0.91 | 1.34 | 0.8 | 1.15 | D | 1, 2, 4
- of which installation and other costs | MUSD/MW_e | 0.58 | 0.56 | 0.54 | 0.53 | 0.49 | 0.72 | 0.43 | 0.62 | D | 1, 2, 4
Fixed O&M | USD/MW_e/year | 41250 | 35898 | 34534 | 34024 | 35063 | 51563 | 30720 | 44128 | B, E | 1
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | E
Technology specific data
Average annual full-load hours | MWh_e/MW_e | 3241 | 3329 | 3416 | 3504 | 2431 | 4052 | 2628 | 4380 |  | 1
Hub Height | meter | 130 | 140 | 150 | 170 | - | - | - | - |  | 1
Rotor Diameter | meter | 150 | 160 | 175 | 190 | - | - | - | - |  | 1
Specific Power | W/m2 | 170 | 174 | 166 | 167 | - | - | - | - |  | 1, 3
Availability | % | 97.2 | 97.7 | 97.7 | 97.7 | - | - | - | -
Water consumption |  | 0 | 0 | 0 | 0 | - | - | - | - |  | 7, 8
Notes:
A | Lower and upper uncertainties are +/- 25%.
B | Costs are projected with a learning rate approach assuming a 5% learning rate based on [6], and 6 % learning rate for OPEX based on [3]. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
C | Lower and upper uncertainties are -15% and +30%.
D | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project. Central value assumes a 65/35 distribution.
E | O&M corresponding to 2.5 % of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
F | This cost estimate represents a general standard onshore wind project in Vietnam. Depending on varying factors like region, terrain, grid connection, transport difficulty, etc. the cost can vary significantly.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
3 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
4 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
5 | Stakeholder dialogue
6 | IEA, 2025 - World Energy Outlook 2025
7 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
8 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains

## Offshore-Fix
Offshore Wind (fixed bottom)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e |  | 15 | 20 | 25 | 12 | 18 | 20 | 35 |  | 1, 2, 5
Generating capacity for a typical power plant | MW_e |  | 500 | 1000 | 1500 | 100 | 1000 | 100 | 2000 |  | 1, 2, 5
Forced outage | % |  | 4 | 3 | 2.5 | 1 | 5 | 1 | 5 | A | 2
Planned outage | % |  | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | A | 2
Technical lifetime | years |  | 27 | 30 | 30 | 25 | 40 | 25 | 40 | B
Construction time | years |  | 3 | 3 | 2.5 | 2.5 | 4 | 2 | 3.5 | C | 2, 3
Space requirement | 1000 m2/MW_e |  | 200 | 167 | 125 | 182 | 222 | 91 | 111 | D | 1
Additional data for non-thermal plants
Capacity factor, theoretical | % |  | 46.5 | 47.2 | 47 | 41.7 | 53.7 | 47 | 57.5 | E
Capacity factor, incl. outages | % |  | 44.5 | 45.7 | 45.7 | 40 | 51.4 | 45.7 | 55.9 | E
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e |  | 4.3 | 3.69 | 3.45 | 3.7 | 5.5 | 2.56 | 4.55 | F, G, H, I | 1, 2, 4, 5, 6
- of which equipment | % |  | 55 | 55 | 55 | - | - | - | - | G, J | 2, 5
- of which installation | % |  | 30 | 30 | 30 | - | - | - | - | G, J | 2, 5
- of which grid connection | % |  | 15 | 15 | 15 | - | - | - | - | G, J | 2, 5
- of which equipment | MUSD/MW_e |  | 2.37 | 2.03 | 1.9 | 2.04 | 3.03 | 1.41 | 2.5 | G, H, I
- of which installation | MUSD/MW_e |  | 1.29 | 1.11 | 1.03 | 1.11 | 1.65 | 0.77 | 1.36 | G, H, I
- of which grid connection | MUSD/MW_e |  | 0.65 | 0.55 | 0.52 | 0.56 | 0.83 | 0.38 | 0.68 | G, H, I
Fixed O&M | USD/MW_e/year |  | 150500 | 133245 | 128736 | 129500 | 192500 | 100000 | 175000 | H, K | 5
Variable O&M | USD/MWh |  | - | - | - | - | - | - | - | K
Technology specific data
Average annual full-load hours | MWh_e/MW_e |  | 3900 | 4000 | 4000 | 3500 | 4500 | 4000 | 4900 | E | 2, 5
Hub Height | m |  | 150 | 170 | 190 | - | - | - | - |  | 1, 2
Rotor Diameter | m |  | 236 | 280 | 320 | - | - | - | - |  | 1, 2
Specific Power | W/m2 |  | 343 | 325 | 311 | - | - | - | - |  | 1, 2
Availability | % |  | 95.7 | 96.7 | 97.2 | - | - | - | -
Avg. water depth | m |  | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 4, 5
Export cable length, per circuit | km |  | 80 | 80 | 80 | 50 | 150 | 50 | 150 |  | 4, 5
Distance to O&M Port | km |  | 65 | 65 | 65 | 45 | 75 | 45 | 75 |  | 4, 5
Water consumption |  |  | 0 | 0 | 0 | - | - | - | - |  | 7, 8
Notes:
General: The datasheet represents a project using AC and monopile as foundation. Data is presented as FID years and 2025 has not been included as the first offshore wind projects will be installed after 2030 with FID close to 2030.
A | Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather.
B | The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
C | Calculated based on average spacing of 8 RD between turbines and a square layout. Space requirement is highly depending on site size, layout and chosen distance between turbines.
D | Construction time is from FID to commercial production.
E | Capacity factor and average annual full load hours depend greatly on the specific project site and can vary a lot. For sites with different wind conditions than 3,900 average annual full load hours mentioned here (for 2030), the capacity factor should be adjusted accordingly.
F | The specific investment cost includes all physical equipment and installation of the turbines (EPC), foundations (monopile), grid connection (excl. grid reinforcements), inter-array cables, offshore substation and export cables to the point of connection at the coastline as well. It excludes VAT and other taxes, financing costs, costs related to renting or buying of land, costs incurred before FID e.g. predevelopment costs (administration, consultancy, project management, site preparations, approvals/permits, etc.), onshore cables and decommissioning costs.
G | Equipment: Cost of turbines, foundations, including transportation. Installation: Electrical infrastructure of turbine, array- and export cables, substation, civil works, planning and management. Grid connection: Cost of export cables and substation. The split of cost may vary considerably from project to project.
H | Cost are projected with a learning rate approach assuming a region-specific learning rate on 10% learning rate from 2030 to 2040, which is lower than the global 15% from IEA WEO 2025 and the 18.3% from [6]. From 2040 to 2050 a learning rate of 15% from IEA WEO 2025 have been applied. The learning rate for OPEX is set at 8% for all years. A lower learning rate was chosen for 2030 to 2040, because the offshore sector in Vietnam is still in early stages of development. There is high uncertainty given the nascent market stage, which could result in higher learnings after the first of a kind (FOAK) project than the 10% included from 2030 to 2040. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
I | Lower uncertainties for 2050 are calculated by using the added capacities from the Net Zero Emissions by 2050 scenario from [9] with a learning rate of 15% from 2030-2050 and the upper uncertainties are calculated by using the added capacities from the Current Policies scenario from [9] with a learning rate of 10% from 2030-2050.
J | The cost breakdown of 55%, 30% and 15% is based on local and regional information, but it can vary significantly based on site characteristics.
K | O&M corresponding to 3.5% of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
References
1 | Danish Energy Agency, 2025 - Danish Technology Catalogue for Generation of Electricity and District Heating
2 | Pre-feasibility studies of projects in Vietnam
3 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
4 | GWEC, 2025 - Innovative Finance Mechanisms for Southeast Asia’s Offshore Wind Take-off: A Study on Unlocking Blended Finance
5 | Bilateral dialogue with local stakeholders
6 | Wood Mackenzie, 2025 - Asia Pacific levelised cost of electricity (LCOE) 2025 report
7 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
8 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains
9 | IEA, 2025 - World Energy Outlook 2025

## Offshore-Floating
Offshore Wind (floating)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e |  | 6 | 8 | 10 | 8 | 15 | 15 | 25 |  | 1, 2
Generating capacity for a typical power plant | MW_e |  | 200 | 500 | 1000 | 50 | 500 | 50 | 3000 |  | 1
Forced outage | % |  | 3 | 2.5 | 2 | 1 | 5 | 1 | 5 |  | 1, 2, 3
Planned outage | % |  | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1, 2, 3
Technical lifetime | years |  | 30 | 30 | 30 | 20 | 35 | 20 | 35 | A | 2, 3
Construction time | years |  | 2.5 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1, 3
Space requirement | 1000 m2/MW_e |  | 279 | 209 | 167 | 251 | 313 | 125 | 200 | B
Additional data for non-thermal plants
Capacity factor, theoretical | % |  | 35.4 | 36.5 | 36.5 | - | - | - | - |  | 1
Capacity factor, incl. outages | % |  | 34.3 | 35.6 | 35.8 | - | - | - | -
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e |  | 5.59 | 4.79 | 4.59 | 5.03 | 6.71 | 2.98 | 6.19 | C, D, E, F | 3, 4
- of which equipment | % |  | 60 | 60 | 60 | - | - | - | - | G
- of which installation | % |  | 30 | 30 | 30 | - | - | - | - | G
- of which grid connection | % |  | 10 | 10 | 10 | - | - | - | - | G
- of which equipment | MUSD/MW_e |  | 3.35 | 2.88 | 2.75 | 3.02 | 4.02 | 1.79 | 3.72 | E, F
- of which installation | MUSD/MW_e |  | 1.68 | 1.44 | 1.38 | 1.51 | 2.01 | 0.89 | 1.86 | E, F
- of which grid connection | MUSD/MW_e |  | 0.56 | 0.48 | 0.46 | 0.5 | 0.67 | 0.3 | 0.62 | E, F
Fixed O&M | USD/MW_e/year |  | 195650 | 167747 | 160607 | 176085 | 234780 | 104394 | 216819 | C, E, H | 2, 3, 4
Variable O&M | USD/MWh |  | - | - | - | - | - | - | - | H
Technology specific data
Average annual full-load hours | MWh_e/MW_e |  | 3007 | 3120 | 3136 | - | - | - | -
Hub height | m |  | 120 | 130 | 140 | - | - | - | -
Rotor diameter | m |  | 164 | 220 | 250 | - | - | - | -
Specific power | W/m2 |  | 284 | 210 | 204 | - | - | - | -
Availability | % |  | 97 | 97.5 | 98 | - | - | - | -
Water consumption |  |  | 0 | 0 | 0 | - | - | - | - | - | 6, 7
Notes:
A | The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine.
B | Calculated based on average spacing of 8 RD between turbines and a square layout. Space requirement is highly depending on site size, layout and chosen distance between turbines.
C | For the initial cost CAPEX and OPEX assessments, it is assumed that Floating offshore is 30% more expensive than fixed bottom offshore.
D | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
E | Costs are projected with a learning rate approach assuming a 10% learning rate based on IEA, and 8% learning rate for OPEX. There is high uncertainty given the nascent market stage, which could result in higher learnings after the first of a kind project. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
F | Lower and upper uncertainties are -10% (lower) and +20% (higher) for 2025 and -/+35% for 2050.
G | Cost breakdown can vary significantly based on site characteristics. Here it is assumed to be the same split as for nearshore wind: 60%, 30% and 10% for equipment based on local (nearshore wind) projects, installation and grid connection are assumed for modelling purposes only.
H | O&M corresponding to 3.5% of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
References
1 | Danish Energy Agency and Ea Energy Analyses, 2023 - Viet Nam Technology Catalogue for Power Generation
2 | Danish Energy Agency, 2025 - Colombian Technology Catalogue for Generation and Storage of Electricity
3 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
4 | IEA, World Energy Outlook, 2025
5 | Danish Energy Agency and Ea Energy Analyses, 2024 - Technology Data for the Indonesian Power Sector: Catalogue for Generation and Storage of Electricity
6 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
7 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains

## Nearshore wind
Offshore Wind (nearshore)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 5 | 6 | 8 | 10 | 4 | 8 | 6 | 15 |  | 1
Generating capacity for a typical power plant | MW_e | 150 | 200 | 300 | 500 | 50 | 500 | 50 | 3000 |  | 1
Forced outage | % | 4 | 3 | 2.5 | 2 | 1 | 5 | 1 | 5 | A
Planned outage | % | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | A
Technical lifetime | years | 27 | 30 | 30 | 30 | 20 | 35 | 20 | 35 | A, B | 1, 2
Construction time | years | 2.5 | 2 | 2 | 1.5 | 1.5 | 4 | 1.5 | 4 |  | 1
Space requirement | 1000 m2/MW_e | 334 | 279 | 209 | 167 | 300 | 375 | 125 | 200 | C | 2
Additional data for non-thermal plants
Capacity factor, theoretical | % | 34.2 | 35.4 | 36.5 | 36.5 | 28.5 | 40 | 32 | 45.7 |  | 1
Capacity factor, incl. outages | % | 32.8 | 34.3 | 35.6 | 35.8 | 28.3 | 38 | 31.6 | 43.4 |  | 1
Economic data (in USD2025)
Specific investment, total system | MUSD/MW_e | 2.7 | 2.38 | 2.11 | 2.04 | 2.43 | 3.24 | 1.32 | 2.75 | D, E, H | 1, 3
- of which equipment | % | 60 | 60 | 60 | 60 | - | - | - | - | F | 1
- of which installation | % | 30 | 30 | 30 | 30 | - | - | - | - | F | 1
- of which grid connection | % | 10 | 10 | 10 | 10 | - | - | - | - | F | 1
- of which equipment | MUSD/MW_e | 1.62 | 1.43 | 1.27 | 1.22 | 1.46 | 1.94 | 1.12 | 1.24
- of which installation | MUSD/MW_e | 0.81 | 0.71 | 0.63 | 0.61 | 0.73 | 0.97 | 0.56 | 0.62
- of which grid connection | MUSD/MW_e | 0.27 | 0.24 | 0.21 | 0.2 | 0.24 | 0.32 | 0.19 | 0.21
Fixed O&M | USD/MW_e/year | 94500 | 86102 | 78662 | 76678 | 40000 | 100000 | 25000 | 45000 | G, H
Variable O&M | USD/MWh | - | - | - | - | - | - | - | - | G
Technology specific data
Average annual full-load hours | MWh_e/MW_e | 3000 | 3100 | 3200 | 3200 | 2500 | 3500 | 2800 | 4000 |  | 1
Hub Height | m | 110 | 120 | 130 | 140 | - | - | - | - |  | 1
Rotor Diameter | m | 145 | 164 | 220 | 250 | - | - | - | - |  | 1
Specific Power | W/m2 | 303 | 284 | 210 | 204 | - | - | - | - |  | 1
Availability | % | 95.7% | 97% | 97.5% | 98% | - | - | - | -
Water consumption |  | 0 | 0 | 0 | 0 | - | - | - | - |  | 4, 5
Notes:
A | There is no substantial difference between intertidal and offshore wind outage and lifetime. However, towing is a less lengthy process.
B | The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine.
C | Calculated based on average spacing of 8 RD between turbines and a square layout. Space requirement is highly depending on site size, layout and chosen distance between turbines.
D | Equipment: Cost of turbines including transportation. Installation: Electrical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
E | Lower and upper uncertainties are -10% (lower) and +20% (higher) for 2025 and -/+35% for 2050.
F | Cost breakdown can vary significantly based on site characteristics. Here 60%, 30% and 10% for equipment based on local projects, installation and grid connection are assumed for modelling purposes only.
G | O&M corresponding to 3.5% of CAPEX/year. All O&M assumed as fixed cost. In reality, some O&M will be variable, but given the high spread in possible capacity factors, all O&M is for simplicity accrued under fixed O&M.
H | Costs are projected with a learning rate approach assuming an 8% learning rate and 6% learning rate for OPEX. There is high uncertainty given the nascent market stage, which could result in higher learnings after the first of a kind project. Learning is linked to the capacity projections of the IEA's World Energy Outlook 2025, with the scenario Stated Policies for the central values and the scenarios Current Policies and Net Zero Emissions by 2050 as base for the upper and lower uncertainty range, respectively.
References
1 | Existing projects in Vietnam
2 | Danish Energy Agency, 2024 - Danish Technology Catalogue for Generation of Electricity and District Heating
3 | Stakeholder dialogue
4 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
5 | U.S. Energy Information Administration, 2023 - U.S. electric power sector continues water efficiency gains

## Tidal-Impoundment
Tidal power - Impoundment Type
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1 | 10 | 25 | 1 | 25 | 1 | 25 | A | 3
Generating capacity for total power plant | MW_e | 30 | 100 | 150 | 10 | 300 | 10 | 300 | B | 3
Electricity efficiency, net, name plate | % | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
Electricity efficiency, net, annual average | % | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
Forced outage | % | 4 | 4 | 4 | 2 | 6 | 2 | 6
Planned outage | weeks per year
Technical lifetime | years | 40 | 40 | 50 | 30 | 120 | 30 | 120 | C | 2
Construction time | years | 5 | 5 | 4 | 4 | 6 | 4 | 6 |  | 3,5
Space requirement | 1000 m2/MW_e | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | D
Additional data for non-thermal plants
Capacity factor, theoretical | % | 35 | 35 | 40 | 35 | 40 | 35 | 40 | E
Capacity factor, incl. outages | %
Ramping configurations
Ramping | % per minute | 50 | 50 | 50 | 30 | 100 | 30 | 100 | G
Minimum load | % of full load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G
Warm start-up time | hours | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
Cold start-up time | hours | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
Environment
PM 2.5 | g/Nm3 | 0 | 0 | 0
SO2 (degree of desulphuring,) | % | 0 | 0 | 0
NOX | g/GJ fuel | 0 | 0 | 0
CH4 | g/GJ fuel | 0 | 0 | 0
N2O | g/GJ fuel | 0 | 0 | 0
Economic data (in USD2025)
Nominal investment | M$/MW_e | 6.8 | 6.4 | 6.3 | 3.6 | 9.3 | 3.6 | 9.3 | E | 1, 2, 4
- of which equipment | %
- of which installation | %
Fixed O&M | $/MWe/year | 88145 | 77811 | 44446 | 29133 | 89639 | 29133 | 89639 | E | 1, 2, 3, 4
Variable O&M | $/MWh | 0 | 0 | 0
Start-up costs | $/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | -
Notes:
A | Based on various projects and company datasheets. The turbine size can vary from project to project based on requirement. The Sihwa Lake project in Korea has 25.4 MW turbines.
B | The capacity is strongly dependent on resources available and shape of coastline. Although a lot of proposed plants are much larger in size, with some being over 2 GW as well, the capacity shown here is based on deployment of plants so far.
C | Actual operational life can be up to 120 years. However, lifetime is taken as 40 years, since there can be significant re-fitting costs after 40 years and discounted cash flows are insignificant after 40 years.
D | Based on information of proposed plants.
E | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
F | Bulb type turbines are commonly used for tidal impoundment plants. The value here is estimated based on efficiencies of bulb type water turbines.
G | Considered as similar to Hydro.
References:
1 | DECC GOV.UK, “The UK 2050 Calculator: Tidal Range Cost Data,” 2011
2 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010
3 | IRENA, “Tidal Energy Technology Brief,” 2014
4 | Pacific Northwest National Laboratory (PNNL), Tethys
5 | Tatiana Montllonch Araquistain, Tidal Power: Economic and Technological assessment

## Tidal-Stream
Tidal power - Stream Type
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1 | 2 | 2 | 0.1 | 6 | 1 | 6 | A | 3, 5
Generating capacity for total power plant | MW_e | 10 | 150 | 150 | 1 | 400 | 1 | 400 | A | 3, 5
Electricity efficiency, net, name plate | % | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2, 3, 5
Electricity efficiency, net, annual average | % | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2, 3, 5
Forced outage | % | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 2
Planned outage | weeks per year
Technical lifetime | years | 25 | 25 | 30 | 20 | 30 | 20 | 30 | B
Construction time | years | 3 | 2 | 2 |  |  |  |  | C
Space requirement | 1000 m2/MW_e
Additional data for non-thermal plants
Capacity factor, theoretical | % | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1, 2, 4
Capacity factor, incl. outages | % | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1, 2, 4
Ramping configurations
Ramping | % per minute | - | - | -
Minimum load | % of full load | - | - | -
Warm start-up time | hours | - | - | -
Cold start-up time | hours | - | - | -
Environment
PM 2.5 | g/Nm3 | 0 | 0 | 0
SO2 (degree of desulphuring,) | % | 0 | 0 | 0
NOX | g/GJ fuel | 0 | 0 | 0
CH4 | g/GJ fuel | 0 | 0 | 0
N2O | g/GJ fuel | 0 | 0 | 0
Economic data (in USD2025)
Nominal investment | M$/MW_e | 7.1 | 5.7 | 4.2 | 3.7 | 8.8 | 2.5 | 8.8 | B | 1, 2, 3
- of which equipment | % | 87 | 87 | 87 | 83 | 91 | 83 | 91 |  | 1, 2
- of which installation | % | 13 | 13 | 13 | 9 | 17 | 9 | 17 |  | 1, 2
Fixed O&M | $/MWe/year | 353105 | 286716 | 142821 | 115410 | 512933 | 115410 | 512933 | B | 1, 2
Variable O&M | $/MWh | 15 | 11 | 9 | [5 empty] | 4
Start-up costs | $/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | -
Notes:
A | Projects are in the early stages, turbines and capacities are smaller. Larger projects are expected to be executed in smaller capacity phases.
B | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
C | Estimated based on MeyGen tidal stream project.
References
1 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK”, 2010
2 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies”, 2015
3 | SIMEC Atlantis Energy, Projects
4 | UK Govt., Electricity Generation Costs 2020 (back calculation from LCOE values)
5 | Pacific Northwest National Laboratory (PNNL), Tethys

## Wave
Wave power
Parameter | Unit | 2025 | 2030 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[5 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 0.2 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.5 | A | 4
Generating capacity for total power plant | MW_e | <1 | 5 | 25 | <1 | 3 | 2 | 75 | B | 1, 4
Electricity efficiency, net, name plate | % | 80 | 80 | 80 | 55 | 95 | 55 | 95 | C | 3
Electricity efficiency, net, annual average | % | 80 | 80 | 80 | 55 | 95 | 55 | 95 | C | 3
Forced outage | % | 10 | 8 | 4 | 2 | 15 | 2 | 5 |  | 1, 2
Planned outage | weeks per year
Technical lifetime | years | 10 | 15 | 25 | 5 | 15 | 20 | 30 |  | 4
Construction time | years | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 4
Space requirement | 1000 m2/MW_e
Additional data for non-thermal plants
Capacity factor, theoretical | % | 30 | 32 | 38 | 20 | 40 | 30 | 45 | A | 1, 2, 3
Capacity factor, incl. outages | % | 30 | 32 | 38 | 20 | 40 | 30 | 45 | A | 1, 2, 3
Ramping configurations
Ramping | % per minute | - | - | -
Minimum load | % of full load | - | - | -
Warm start-up time | hours | - | - | -
Cold start-up time | hours | - | - | -
Environment
PM 2.5 | g/Nm3 | 0 | 0 | 0
SO2 (degree of desulphuring,) | % | 0 | 0 | 0
NOX | g/GJ fuel | 0 | 0 | 0
CH4 | g/GJ fuel | 0 | 0 | 0
N2O | g/GJ fuel | 0 | 0 | 0
Economic data (in USD2025)
Nominal investment | M$/MW_e | 13.4 | 10.6 | 6.8 | 5.1 | 23.2 | 3.4 | 11.6 |  | 1, 5, 7
- of which equipment | % | 87 | 87 | 87 | 85 | 90 | 85 | 90 |  | 1, 6
- of which installation | % | 13 | 13 | 13 | 10 | 15 | 10 | 15 |  | 1, 6
Fixed O&M | $/MWe/year | 615022 | 384700 | 288836 | 179278 | 1052011 | 89639 | 486788 |  | 1, 5
Variable O&M | $/MWh
Start-up costs | $/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | - | - | - | -
Notes:
A | Many different types of converters and system designs are being researched and tested, and the industry has not converged on a specific design.
B | Number of small units are combined to setup a large wave farm. With time it can be expected to have larger unit sizes and also large wave farm configurations.
C | Depends on the power-take-off system. Many configurations are being explored and that is why there is a wide range.
References
1 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies”, 2015
2 | IRENA, "Wave Energy Technology Brief", 2014
3 | Aderinto and Li, Review on Power Performance and Efficiency of Wave Energy Converters, 2019
4 | Danish Energy Agency, Technology Data - Generation of Electricity and District Heating, 2024
5 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK”, 2010
6 | Carbon Trust, Future Marine Energy, 2010
7 | Intelligent Energy Systems (IES) and Mekong Economics (MKE), Alternatives for Power Generation in the Greater Mekong Sub-Region, 2014

## Biomass power plant
Biomass power plant
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 25 | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
Generating capacity for total power plant | MW_e | 25 | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1,5
Electrical efficiency, net, name plate | % | 32 | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1, 3, 7
Electrical efficiency, net, annual average | % | 31 | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1, 3, 7
Forced outage | % | 7 | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 |  | 1
Planned outage | weeks per year | 6 | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 |  | 1
Self-consumption | %
Technical lifetime | years | 25 | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 |  | 7, 8
Construction time | years | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 7
Space requirement | 1000_m2/MW_e | 35 | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 |  | 1, 9
Additional data for non-thermal plants
Capacity factor, theoretical | %
Capacity factor, incl. outages | %
Ramping ability
Ramping | % of full load/minute | 10 | 10 | 10 | 10 | [5 empty] | 3
Minimum load | % of full load | 30 | 30 | 30 | 30 | [5 empty] | 3
Warm start-up time | hours | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Cold start-up time | hours | 10 | 10 | 10 | 10 | [5 empty] | 3
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i | 125 | [8 empty] | 3
SO2 (degree of desulphuring) | % | 0 | [8 empty] | 3
NOX | g/GJ_i | 125 | [8 empty] | 3
CH4 | g/GJ_i
N2O | g/GJ_i
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 2.23 | 2.19 | 2.14 | 2.12 | 1.67 | 3.01 | 1.59 | 2.65 | A | 4, 5, 6, 7, 8
- of which equipment | % | 65 | 65 | 65 | 65 | 50 | 85 | 50 | 85
- of which installation and other costs | % | 35 | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1, 2
- of which equipment | MUSD/MW_e | 1.45 | 1.43 | 1.39 | 1.38 | 0.83 | 2.55 | 0.8 | 2.25 |  | 1, 2
- of which installation and other costs | MUSD/MW_e | 0.78 | 0.77 | 0.75 | 0.74 | 0.25 | 1.5 | 0.24 | 1.33
Fixed O&M | USD/MW_e/year | 61627 | 60745 | 59371 | 58744 | 46220 | 83196 | 44058 | 73430 | A | 4, 5, 8
Variable O&M | USD/MWh | 3.98 | 3.93 | 3.84 | 3.8 | 2.99 | 5.38 | 2.85 | 4.75 | A | 5
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 2100 | 2100 | 2100 | 2100 | - | - | - | - | B, C | 10, 11, 12, 13
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming a cooling tower is used. Pond- and once-through cooling result in lower water consumption.
C | Depending on the cooling method and the assumptions in different references, the water consumption can vary between ~1400 and 42200 L/MWh.
References
1 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024.
2 | ASEAN Centre of Energy, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states", 2016.
3 | Danish Energy Agency and COWI, "Technology catalogue for biomass to energy", 2017.
4 | IRENA, "Renewable power generation cost in 2014", 2015
5 | IFC and BMF, "Converting biomass to energy - A guide for developers and investors", 2017.
6 | OJK, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, 2014.
7 | IEA-ETSAP and IRENA, "Biomass for Heat and Power, Technology Brief", 2015.
8 | PKPPIM, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia, 2014.
9 | India Central Electricity Authority, "Report on the Land Requirement of Thermal Power Stations", 2007.
10 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity
Generating Technologies
11 | U.S. Energy Information Administration, 2024 - Thermoelectric cooling water data
12 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
13 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025

## MSW-Incineration Power Plant
Incineration Power Plant - Municipal Solid Waste
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 22 | 22 | 22 | 23
Generating capacity for total power plant | MW_e | 22 | 22 | 22 | 23
Electrical efficiency, net, name plate | % | 29 | 30 | 30 | 31 | 28 | 32 | 30 | 33 |  | 1
Electrical efficiency, net, annual average | % | 28 | 29 | 29 | 29 | 26 | 30 | 28 | 31 |  | 1
Forced outage | % | 1 | 1 | 1 | 1 | [5 empty] | 1
Planned outage | % | 6 | 6 | 6 | 6 | [5 empty] | 1
Self-consumption | % | [9 empty] | 1
Technical lifetime | years | 25 | 25 | 25 | 25 | [5 empty] | 1
Construction time | years | 2.5 | 2.5 | 2.5 | 2.5 | [5 empty] | 1
Space requirement | 1000_m2/MW_e | 1.5 | 1.5 | 1.5 | 1.5
Additional data for non-thermal plants
Capacity factor, theoretical | %
Capacity factor, incl. outages | %
Ramping ability
Ramping | % of full load/minute | 10 | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 |  | 1
Minimum load | % of full load | 20 | 20 | 20 | 20 | 15 | 25 | 15 | 25 |  | 1
Warm start-up time | hours | 50 | 50 | 50 | 50 | 0.4 | 0.6 | 0.4 | 0.6 |  | 1
Cold start-up time | hours | 200 | 200 | 200 | 200 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i
SO2 (degree of desulphuring) | %
NOX | g/GJ_i
CH4 | g/GJ_i
N2O | g/GJ_i
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 6.97 | 6.47 | 6.1 | 5.73 | 5.23 | 9.41 | 4.3 | 7.16 | A | 1
- of which equipment | % | 60 | 60 | 60 | 60 | 45 | 75 | 45 | 75 |  | 1
- of which installation and other costs | % | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 1
- of which equipment | MUSD/MW_e | 4.18 | 4.14 | 4.06 | 3.98 | 3.14 | 5.65 | 2.98 | 4.97 | A | 1
- of which installation and other costs | MUSD/MW_e | 2.79 | 2.76 | 2.71 | 2.65 | 2.09 | 3.76 | 1.99 | 3.32 | A | 1
Fixed O&M | USD/MW_e/year | 315479 | 312337 | 306146 | 300078 | 236609 | 425896 | 225058 | 375097 | A | 1
Variable O&M | USD/MWh | 31.25 | 30.94 | 30.32 | 29.72 | 23.44 | 42.19 | 22.29 | 37.15 | A | 1
Start-up costs | USD/MW_e/start-up
Technology specific data
Waste treatment capacity | tonnes/h | 27.7 | 27.7 | 27.7 | 27.7
Calorific content | GJ/ton
Investment cost (waste) | $/ton
Water Consumption | L/MWh | 600 | 600 | 600 | 600 | - | - | - | - | B, C | 2
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming the energy value for MSW is 10 MJ/kg and the plant efficiency is 30%.
C | Flue gas wet scrubbing not included. If it is included, the water consumption can be higher.
References
1 | Danish Energy Agency, Danish Technology Catalogue “Technology Data for Energy Plants”, 2024
2 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025

## MSW-Landfill Gas Power Plant
Landfill Gas Power Plant - Municipal Solid Waste
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1 | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
Generating capacity for total power plant | MW_e | 1 | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
Electrical efficiency, net, name plate | % | 35 | 35 | 35 | 35 | 25 | 37 | 25 | 37 |  | 2
Electrical efficiency, net, annual average | % | 34 | 34 | 34 | 34 | 25 | 37 | 25 | 37 |  | 2
Forced outage | % | 5 | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
Planned outage | % | 9.6 | 9.6 | 9.6 | 9.6 | 2 | 15 | 2 | 15 |  | 4
Self-consumption | %
Technical lifetime | years | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 |  | 3
Space requirement | 1000_m2/MW_e
Additional data for non-thermal plants
Capacity factor, theoretical | %
Capacity factor, incl. outages | %
Ramping ability
Ramping | % of full load/minute
Minimum load | % of full load
Warm start-up time | hours
Cold start-up time | hours
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i
SO2 (degree of desulphuring) | %
NOX | g/GJ_i
CH4 | g/GJ_i
N2O | g/GJ_i
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 3.24 | 3.2 | 3.14 | 3.08 | 2.43 | 4.37 | 2.8 | 3.54 |  | 3
- of which equipment | % | 70 | 70 | 70 | 70 | 64 | 77 | 64 | 81 |  | 5
- of which installation and other costs | % | 30 | 30 | 30 | 30 | 27 | 33 | 27 | 35 |  | 5
- of which equipment | MUSD/MW_e | 2.27 | 2.24 | 2.2 | 2.16 | 1.54 | 3.36 | 1.47 | 2.96 |  | 5
- of which installation and other costs | MUSD/MW_e | 0.97 | 0.96 | 0.94 | 0.92 | 0.66 | 1.44 | 0.63 | 1.27 |  | 5
Fixed O&M | USD/MW_e/year | 161848 | 160236 | 157060 | 153947 | 121386 | 218495 | 139952 | 177039 |  | 3
Variable O&M | USD/MWh | 0 | 0 | 0 | 0
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 2270 | 2270 | 2270 | 2270 | - | - | - | - | A | 6
Notes:
A | Assuming a cooling tower is used. For pond-cooling, it is a bit lower, around 1970 L/MWh.
References
1 | OJK, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, Jakarta, Indonesia, 2014
2 | Renewables Academy" (RENAC) AG, "Biogas Technology and Biomass", Berlin, Germany, 2014
3 | IEA-ETSAP and IRENA, "Biomass for Heat and Power, Technology Brief", 2015
4 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024
5 | MEMR, "Waste to Energy Guidebook", Jakarta, Indonesia, 2015
6 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025

## Biogas power plant
Biogas power plant
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1 | 1 | 1 | 1 | [5 empty] | 3
Generating capacity for total power plant | MW_e | 1 | 1 | 1 | 1 | [5 empty] | 3
Electrical efficiency, net, name plate | % | 35 | 35 | 35 | 35 | [5 empty] | 4
Electrical efficiency, net, annual average | % | 34 | 34 | 34 | 34 | [5 empty] | 4
Forced outage | % | 5 | 5 | 5 | 5 | [5 empty] | 1
Planned outage | % | 9.6 | 9.6 | 9.6 | 9.6 | [5 empty] | 1
Self-consumption | %
Technical lifetime | years | 25 | 25 | 25 | 25 | [5 empty] | 7
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | [5 empty] | 7
Space requirement | 1000_m2/MW_e | 70 | 70 | 70 | 70 | [5 empty] | 12
Additional data for non-thermal plants
Capacity factor, theoretical | %
Capacity factor, incl. outages | %
Ramping ability
Ramping | % of full load/minute | 20 | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 11, 13
Minimum load | % of full load | 40 | 30 | 23 | 15 | 30 | 50 | 10 | 20 |  | 10, 13
Warm start-up time | hours
Cold start-up time | hours
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i
SO2 (degree of desulphuring) | %
NOX | g/GJ_i
CH4 | g/GJ_i |  | 0 | 0 | 0 |  |  | 0 | 0
N2O | g/GJ_i |  | 0 | 0 | 0 |  |  | 0 | 0
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 3.6 | 3.6 | 3.5 | 3.4 | 2.71 | 4.87 | 2.58 | 4.3 | A | 3, 5, 8, 9
- of which equipment | % | 65 | 65 | 65 | 65 | 50 | 85 | 50 | 85
- of which installation and other costs | % | 35 | 35 | 35 | 35 | 15 | 50 | 15 | 50
- of which equipment | MUSD/MW_e | 2.35 | 2.31 | 2.26 | 2.24 | 1.35 | 4.14 | 1.29 | 3.66
- of which installation and other costs | MUSD/MW_e | 1.26 | 1.25 | 1.22 | 1.2 | 0.41 | 2.44 | 0.39 | 2.15
Fixed O&M | USD/MW_e/year | 125494 | 123699 | 120900 | 119625 | 94121 | 169417 | 89718 | 149531 | A | 5, 7, 9
Variable O&M | USD/MWh | 0.12 | 0.12 | 0.12 | 0.12 | 0.09 | 0.17 | 0.09 | 0.15 | A | 6, 9
Start-up costs | USD/MW_e/start-up
Technology specific data
Water consumption | L/MWh | 2100 | 2100 | 2100 | 2100 | - | - | - | - | B | 14, 15
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming a cooling tower is used.
References
1 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024
2 | ASEAN Centre of Energy, Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states, 2016
3 | Winrock, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International, 2015
4 | RENAC, "Biogas Technology and Biomass, Renewables Academy (RENAC)", 2014
5 | IFC and BMF, Converting biomass to energy - A guide for developers and investors", 2017
6 | OJK, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, 2014
7 | IEA-ETSAP and IRENA, "Biomass for Heat and Power, Technology Brief", 2015
8 | PKPPIM, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia, 2014
9 | Learning curve approach for the development of financial parameters
10 | Vuorinen, A, "Planning of Optimal Power Systems", 2008
11 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016
12 | Chazaro Gerbang Internasional, "Utilization of Biogas Generated from the Anaerobic Treatment of Palm Oil Mills Effluent (POME) as Indigenous Energy Source for Rural Energy Supply and Electrification - A Pre-Feasibility Study Report", 2004
13 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025
14 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
15 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## ICE-Dual fuel
Internal combustion engine – dual fuel (diesel & gas)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 20 | 20 | 20 | 20 | - | - | - | - |  | 9
Generating capacity for total power plant | MW_e | 100 | 100 | 100 | 100 | - | - | - | -
Electrical efficiency, net, name plate (gas mode) | % | 45.5 | 46.5 | 47.5 | 47.5 | 43.5 | 47.5 | 45.5 | 52.5 |  | 9, 10
Electrical efficiency, net, annual average (gas mode) | % | 44.5 | 45.5 | 46.5 | 46.5 | 42.5 | 46.5 | 44.5 | 51.5 |  | 9, 10
Electrical efficiency, net, name plate | % | 44 | 45 | 46 | 46 | 42 | 46 | 44 | 51 |  | 9, 10
Electrical efficiency, net, annual average | % | 43 | 44 | 45 | 45 | 41 | 45 | 43 | 50 |  | 9, 10
Forced outage | % | 3 | 3 | 3 | 3 | - | - | - | -
Planned outage | % | 1.9 | 1.9 | 1.9 | 1.9 | - | - | - | - |  | 1
Self-consumption | % | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Technical lifetime | years | 50 | 50 | 50 | 50 | - | - | - | - |  | 10
Construction time | years | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Space requirement | 1000_m2/MW_e | 0.05 | 0.05 | 0.05 | 0.05 | - | - | - | - |  | 1
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 100 | 100 | 100 | 100 | - | - | - | - |  | 7, 8, 9
Minimum load | % of full load | 2 | 2 | 2 | 2 | - | - | - | - | A | 10
Warm start-up time | hours | 0.03 | 0.03 | 0.03 | 0.03 | - | - | - | - |  | 7, 8, 9, 10
Cold start-up time | hours | 0.2 | 0.2 | 0.2 | 0.2 | - | - | - | - |  | 7, 8, 9
Environment
PM 2.5 | g/Nm3 | 20 | 20 | 20 | 20 | - | - | - | - |  | 2, 3
SO2 (degree of desulphuring) | % | 0 | 0 | 0 | 0 | - | - | - | - |  | 2, 3
NOX | g/GJ_i | 280 | 280 | 280 | 280 | - | - | - | - |  | 2, 3
CH4 | g/GJ_i | - | - | - | - | - | - | - | -
N2O | g/GJ_i | - | - | - | - | - | - | - | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.91 | 0.9 | 0.88 | 0.87 | 0.83 | 1.17 | 0.79 | 1.11 |  | 5, 6, 8, 9, 10
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | -
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | -
- of which equipment | MUSD/MW_e | 0.59 | 0.58 | 0.57 | 0.56 | - | - | - | - |  | 10
- of which installation and other costs | MUSD/MW_e | 0.32 | 0.32 | 0.31 | 0.3 | - | - | - | - |  | 10
Fixed O&M | USD/MW_e/year | 10000 | 9900 | 9704 | 9512 | - | - | - | - |  | 1, 8, 9
Variable O&M | USD/MWh | 8.89 | 8.8 | 8.63 | 8.46 | - | - | - | - |  | 1, 8, 9, 10
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
Notes:
A | Minimum load for a single unit is 10 % - corresponds to 2 % for total plant when consisting of 5 units.
B | Since cooling system is closed-looped, the water consumption is negligible.
References
1 | Danish Energy Agency, "Technology Data for Energy Plants", 2016.
2 | Minister of Environment of Indonesia, Regulation 21/2008.
3 | The International Council on Combustion Engines, Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2, 2008.
4 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
5 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
6 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for “Generation and Storage of Electricity", 2024
7 | IRENA, Flexibility in Conventional Power Plants, 2019.
https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Flexibility_in_CPPs_2019
8 | Danish Energy Agency, "Technology Data - Generation of Electricity and District Heating", 2024
9 | Wärtsila, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants, 2011.
10 | Stakeholder input

## ICE-Natural gas
Internal combustion engine (natural gas only)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 20 | 20 | 20 | 20 | - | - | - | - |  | 9
Generating capacity for total power plant | MW_e | 100 | 100 | 100 | 100 | - | - | - | -
Electrical efficiency, net, name plate | % | 45.5 | 46.5 | 47.5 | 47.5 | 43.5 | 47.5 | 45.5 | 52.5 |  | 8, 9, 10
Electrical efficiency, net, annual average | % | 44.5 | 45.5 | 46.5 | 46.5 | 42.5 | 46.5 | 44.5 | 51.5 |  | 8, 9, 10
Forced outage | % | 3 | 3 | 3 | 3 | - | - | - | -
Planned outage | % | 1.9 | 1.9 | 1.9 | 1.9 | - | - | - | - |  | 1
Self-consumption | % | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Technical lifetime | years | 50 | 50 | 50 | 50 | - | - | - | - |  | 10
Construction time | years | 2 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Space requirement | 1000_m2/MW_e | 0.16 | 0.16 | 0.16 | 0.16 | - | - | - | -
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 100 | 100 | 100 | 100 | - | - | - | - |  | 7, 8, 9
Minimum load | % of full load | 2 | 2 | 2 | 2 | - | - | - | - | A | 10
Warm start-up time | hours | 0.03 | 0.03 | 0.03 | 0.03 | - | - | - | - |  | 7, 8, 9, 10
Cold start-up time | hours | 0 | 0 | 0 | 0 | - | - | - | -
Environment
PM 2.5 | g/Nm3 | 7.5 | 7.5 | 7.5 | 7.5 | - | - | - | - |  | 2, 3, 8, 9
SO2 (degree of desulphuring) | % | 0 | 0 | 0 | 0 | - | - | - | - |  | 2, 3
NOX | g/GJ_i | 125 | 125 | 125 | 125 | - | - | - | - |  | 2, 3, 8, 9
CH4 | g/GJ_i | - | - | - | - | - | - | - | -
N2O | g/GJ_i | - | - | - | - | - | - | - | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.85 | 0.84 | 0.82 | 0.81 | 0.78 | 1.2 | 0.74 | 1.14 |  | 5, 6, 8, 9, 10
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | -
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | -
- of which equipment | MUSD/MW_e | 0.55 | 0.54 | 0.53 | 0.52 | - | - | - | - |  | 10
- of which installation and other costs | MUSD/MW_e | 0.3 | 0.3 | 0.29 | 0.29 | - | - | - | - |  | 10
Fixed O&M | USD/MW_e/year | 10000 | 9900 | 9704 | 9512 | - | - | - | - |  | 1, 8, 9
Variable O&M | USD/MWh | 8.09 | 8.01 | 7.85 | 7.7 | - | - | - | - |  | 1, 8, 9, 10
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | L/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B
Notes:
A | Minimum load for a single unit is 10 % - corresponds to 2 % for total plant when consisting of 5 units.
B | Since cooling system is closed-looped, the water consumption is negligible.
References:
1 | Danish Energy Agency, "Technology Data for Energy Plants", 2016
2 | Minister of Environment of Indonesia, Regulation 21/2008
3 | The International Council on Combustion Engines, Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2, 2008
4 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
5 | BWSC once again to deliver highly efficient power plant in the Faroe Islands
6 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2017
7 | IRENA, Flexibility in Conventional Power Plants, 2019,
https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Flexibility_in_CPPs_2019
8 | Danish Energy Agency, "Technology Data - Generation of Electricity and District Heating", 2020
9 | Wärtsila, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants, 2011
10 | Stakeholder input

## ICE-Oil
Diesel engine (using fuel oil)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 20 | 20 | 20 | 20 | - | - | - | - |  | 9
Generating capacity for total power plant | MW_e | 100 | 100 | 100 | 100 | - | - | - | -
Electrical efficiency, net, name plate | % | 44 | 45 | 46 | 46 | 42 | 46 | 44 | 51 |  | 9, 10
Electrical efficiency, net, annual average | % | 43 | 44 | 45 | 45 | 41 | 45 | 43 | 50 |  | 9, 10
Forced outage | % | 3 | 3 | 3 | 3 | - | - | - | -
Planned outage | % | 1.9 | 1.9 | 1.9 | 1.9 | - | - | - | - |  | 1
Self-consumption | % | 1.5 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Technical lifetime | years | 50 | 50 | 50 | 50 | - | - | - | - |  | 10
Construction time | years | 2 | 1.5 | 1.5 | 1.5 | - | - | - | - |  | 10
Space requirement | 1000_m2/MW_e | 0.05 | 0.05 | 0.05 | 0.05 | - | - | - | - |  | 1
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 100 | 100 | 100 | 100 | - | - | - | - |  | 7, 8, 9
Minimum load | % of full load | 2 | 2 | 2 | 2 | - | - | - | - | A | 10
Warm start-up time | hours | 0.03 | 0.03 | 0.03 | 0.03 | - | - | - | - |  | 7, 8, 9, 10
Cold start-up time | hours | 0.2 | 0.2 | 0.2 | 0.2 | - | - | - | - |  | 7, 8, 9
Environment
PM 2.5 | g/Nm3 | 20 | 20 | 20 | 20 | - | - | - | - |  | 2, 3
SO2 (degree of desulphuring) | % | 0 | 0 | 0 | 0 | - | - | - | - |  | 2, 3
NOX | g/GJ_i | 280 | 280 | 280 | 280 | - | - | - | - |  | 2, 3
CH4 | g/GJ_i | - | - | - | - | - | - | - | -
N2O | g/GJ_i | - | - | - | - | - | - | - | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 0.8 | 0.79 | 0.78 | 0.76 | 0.73 | 1.13 | 0.7 | 1.07 |  | 5, 6, 7, 8, 10
- of which equipment | % | 65 | 65 | 65 | 65 | - | - | - | -
- of which installation and other costs | % | 35 | 35 | 35 | 35 | - | - | - | -
- of which equipment | MUSD/MW_e | 0.52 | 0.51 | 0.5 | 0.49 | - | - | - | -
- of which installation and other costs | MUSD/MW_e | 0.28 | 0.28 | 0.27 | 0.27 | - | - | - | -
Fixed O&M | USD/MW_e/year | 10000 | 9900 | 9704 | 9512 | - | - | - | - |  | 1, 8, 9
Variable O&M | USD/MWh | 8.09 | 8.01 | 7.85 | 7.7 | - | - | - | - |  | 1, 8, 9, 10
Start-up costs | USD/MW_e/start-up | - | - | - | - | - | - | - | -
Technology specific data
Water consumption | l/MWh | - | - | - | - | - | - | - | - | B
Notes:
A | Minimum load for a single unit is 10 % - corresponds to 2 % for total plant when consisting of 5 units.
B | Since cooling system is closed-looped, the water consumption is negligible.
References
1 | Danish Energy Agency, "Technology Data for Energy Plants", 2016
2 | Minister of Environment of Indonesia, Regulation 21/2008
3 | The International Council on Combustion Engines, Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2, 2008
4 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
5 | BWSC once again to deliver highly efficient power plant in the Faroe Islands
6 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2017
7 | IRENA, Flexibility in Conventional Power Plants, 2019,
https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Flexibility_in_CPPs_2019
8 | Danish Energy Agency, "Technology Data - Generation of Electricity and District Heating", 2020
9 | Wärtsila, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants, 2011.
10 | Stakeholder input

## Geothermal Small
Geothermal Small (binary/condensing)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 10 | 10 | 10 | 10 | 0.3 | 30 | 0.3 | 30 |  | 5, 11
Generating capacity for total power plant | MW_e | 20 | 20 | 20 | 20 | 5 | 30 | 5 | 30 |  | 5
Electrical efficiency, net, name plate | % | 10 | 11 | 12 | 12 | 6 | 12 | 8 | 14 |  | 8
Electrical efficiency, net, annual average | % | 10 | 11 | 12 | 12 | 6 | 12 | 8 | 14 |  | 8
Forced outage | % | 10 | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 5
Planned outage | % | 7.7 | 7.7 | 7.7 | 7.7 | 4 | 12 | 4 | 12 |  | 5
Self-consumption | % | [6 empty] | 0 | 0 |  | 5
Technical lifetime | years | 30 | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 5
Construction time | years | 2 | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 5
Space requirement | 1000_m2/MW_e | 30 | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 5
Additional data for non-thermal plants
Capacity factor, theoretical | % | 90 | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 5
Capacity factor, incl. outages | % | 80 | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 5
Ramping ability
Ramping | % of full load/minute
Minimum load | % of full load
Warm start-up time | hours
Cold start-up time | hours
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i
SO2 (degree of desulphuring) | %
NOX | g/GJ_i
CH4 | g/GJ_i
N2O | g/GJ_i
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 5.85 | 5.67 | 5.42 | 5.26 | 4.39 | 7.9 | 3.95 | 6,58 | A | 5, 6, 7, 11
- of which equipment | % | 60 | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 6
- of which installation and other costs | % | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 6
- of which equipment | MUSD/MW_e | 3.51 | 3.4 | 3.25 | 3.16 | 1.76 | 5.53 | 1.58 | 4.97 |  | 6
- of which installation and other costs | MUSD/MW_e | 2.34 | 2.27 | 2.17 | 2.11 | 1.32 | 3.95 | 1.18 | 3.55 |  | 6
Fixed O&M | USD/MW_e/year | 25896 | 25095 | 23986 | 23296 | 19422 | 34959 | 17472 | 29120 | A | 5, 7
Variable O&M | USD/MWh | 0.47 | 0.46 | 0.44 | 0.43 | 0.35 | 0.64 | 0.32 | 0.53 | A | 5, 7
Technology specific data
Exploration cost | MUSD/MW_e | 0.19 | 0.19 | 0.19 | 0.19 | 0.14 | 0.25 | 0.14 | 0.23 |  | 10
Confirmation cost | MUSD/MW_e | 0.19 | 0.19 | 0.19 | 0.19 | 0.14 | 0.25 | 0.14 | 0.23 |  | 10
Capacity expansion cost of nominal investment | %
Water consumption | L/MWh | 9770 | 9770 | 9770 | 9770 | - | - | - | - | B | 1, 2, 3
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming a cooling tower is used, binary. Different ranges can be found.
References
1 | International Energy Agency, 2016 - Water Energy Nexus
2 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
3 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
4 | Budisulistyo & Krumdieck, "Thermodynamic and economic analysis for the pre- feasibility study of a binary geothermal power plant", 2014
5 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity", 2024
6 | IRENA, Renewable Power Generation Costs in 2014, 2015
7 | Learning curve approach for the development of financial parameters
8 | Moon & Zarrouk, “Efficiency Of Geothermal Power Plants: A Worldwide Review”, 2012
9 | Yuniarto, et. al. “Geothermal Power Plant Emissions in Indonesia”, 2015
10 | Geothermal Energy Association, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy", 2006
11 | Climate Policy Initiative, Using Private Finance to Accelerate Geothermal Deployment: Sarulla Geothermal Power Plant, Indonesia, 2015

## Geothermal Large
Geothermal Large (flash/dry)
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 55 | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 4
Generating capacity for total power plant | MW_e | 110 | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 4
Electrical efficiency, net, name plate | % | 16 | 16 | 16 | 16 | 8 | 18 | 10 | 20 |  | 8
Electrical efficiency, net, annual average | % | 15 | 15 | 15 | 15 | 8 | 18 | 10 | 20 |  | 8
Forced outage | % | 10 | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 4
Planned outage | % | 7.7 | 7.7 | 7.7 | 7.7 | 2 | 6 | 2 | 6 |  | 4
Self-consumption | %
Technical lifetime | years | 30 | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 4
Construction time | years | 2 | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 4
Space requirement | 1000_m2/MW_e | 30 | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 4
Additional data for non-thermal plants
Capacity factor, theoretical | % | 90 | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 4
Capacity factor, incl. outages | % | 80 | 80 | 80 | 80 | 45 | 93 | 45 | 93 |  | 4
Ramping ability
Ramping | % of full load/minute | 3 | 10 | 15 | 20 | [5 empty] | 11
Minimum load | % of full load
Warm start-up time | hours
Cold start-up time | hours
Minimum Up time | hours
Minimum Down time | hours
Environment
PM 2.5 | g/GJ_i
SO2 (degree of desulphuring) | %
NOX | g/GJ_i
CH4 | g/GJ_i
N2O | g/GJ_i
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 4.5 | 4.34 | 4.15 | 4.03 | 3.36 | 6.05 | 3.02 | 5.04 | A | 4, 5, 6, 7
- of which equipment | % | 60 | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 6
- of which installation and other costs | % | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 6
- of which equipment | MUSD/MW_e | 2.69 | 2.61 | 2.49 | 2.42 | 1.34 | 4.24 | 1.21 | 3.53 |  | 6
- of which installation and other costs | MUSD/MW_e | 1.79 | 1.74 | 1.66 | 1.61 | 1.01 | 3.03 | 0.91 | 2.52 |  | 6
Fixed O&M | USD/MW_e/year | 23281 | 22561 | 21564 | 20944 | 17461 | 31430 | 15707 | 26179 | A | 4, 7
Variable O&M | USD/MWh | 0.32 | 0.31 | 0.3 | 0.29 | 0.24 | 0.44 | 0.22 | 0.36 | A | 4, 7
Technology specific data
Exploration cost | MUSD/MW_e | 0.19 | 0.19 | 0.19 | 0.19 | 0.14 | 0.23 | 0.14 | 0.23 |  | 10
Confirmation cost | MUSD/MW_e | 0.19 | 0.19 | 0.19 | 0.19 | 0.14 | 0.23 | 0.14 | 0.23 |  | 10
Capacity expansion cost of nominal investment | %
Water consumption | L/MWh | 13620 | 13620 | 13620 | 13620 | - | - | - | - | B | 1, 2, 3
Notes:
A | Uncertainty (Upper/Lower) is estimated as -25% (lower) and +35% (higher) for 2025 and +/- 25% for 2050.
B | Assuming a cooling tower is used, flash (geothermal fluid). Flash (freshwater) results in lower water consumption. Different ranges can be found
References
1 | International Energy Agency, 2016 - Water Energy Nexus
2 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
3 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity
4 | Ea Energy Analyses and Danish Energy Agency, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and
Storage of Electricity", 2024
5 | IEA, World Energy Outlook, 2025
6 | IRENA, Renewable Power Generation Costs in 2014, 2015
7 | Learning curve approach for the development of financial parameters
8 | Moon & Zarrouk, “Efficiency Of Geothermal Power Plants: A Worldwide Review”, 2012
9 | Yuniarto, et. al. “Geothermal Power Plant Emissions in Indonesia”, 2015
10 | Geothermal Energy Association, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy", 2006
11 | Geothermal Energy Association, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from
Geothermal Facilities", 2015

## Nuclear PWR
Nuclear PWR
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 1200 | 1200 | 1200 | 1200 |  |  |  |  | F
Generating capacity for total power plant | MW_e | 2400 | 2400 | 2400 | 2400 |  |  |  |  | A
Electrical efficiency, net, name plate | % | 36 | 38 | 40 | 42 |  |  |  |  | B | 1
Electrical efficiency, net, annual average | % | 34 | 36 | 38 | 40 |  |  |  |  | B | 1
Forced outage | % | 2 | 2 | 2 | 2 |  |  |  |  | C | 1
Planned outage | % | 9 | 8 | 7 | 6 | [5 empty] | 1
Self-consumption | % | 7 | 7 | 6 | 5 |  |  |  |  | N | 14
Technical lifetime | years | 60 | 60 | 60 | 60 | 40 | 80 |  |  |  | 1, 2
Construction time | years | 7.4 | 7.4 | 7.4 | 7.4 | 4 | 10 |  |  | D | 1, 2
Space requirement | 1000_m2/MW_e | 2.6 | 2.6 | 2.6 | 2.6 | 2 | 3.4 | 2 | 3.4 | E | 3, 4
Additional data for non-thermal plants
Capacity factor, theoretical | % | 85 | 87 | 88 | 90 | 75 | 93 |  |  |  | 5, 6, 7
Capacity factor, incl. outages | % | 76 | 78 | 80 | 83 | 67 | 83 |  |  |  | 5, 6, 7
Ramping ability
Ramping | % of full load/minute | 4 | 4 | 3 | 3 | 3 | 5 |  |  | F, G | 1, 8
Minimum load | % of full load | 40 | 40 | 40 | 40 | 30 | 50 |  |  | G | 8
Warm start-up time | hours | 2 | 2 | 1 | 1 | 2 | 6 |  |  |  | 8
Cold start-up time | hours | 30 | 30 | 30 | 30 | 24 | 48 |  |  |  | 1
Environment
PM 2.5 | g/GJ_i | -
SO2 (degree of desulphuring) | % | -
NOX | g/GJ_i | -
CH4 | g/GJ_i | -
N2O | g/GJ_i | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | 6.5 | 6 | 5.5 | 5 | 5 | 10 | 4.5 | 8 | H, I, J, K | 6, 7, 9, 10, 11
- of which equipment | % | 40 | 40 | 40 | 40 | - | - | - | - | I
- of which installation and other costs | % | 60 | 60 | 60 | 60 | - | - | - | - | I
- of which equipment | MUSD/MW_e | 2.6 | 2.4 | 2.2 | 2 | 2 | 4 | 1.8 | 3.2 | I
- of which installation and other costs | MUSD/MW_e | 3.9 | 3.6 | 3.3 | 3 | 3 | 6 | 2.7 | 4.8 | I
Fixed O&M | USD/MW_e/year | 127000 | 122000 | 118000 | 113000 | 50000 | 180000 | 50000 | 180000 |  | 9, 10
Variable O&M | USD/MWh | 2.4 | 2.3 | 2.2 | 2.1 | 1.8 | 3 | 1.6 | 2.6 | L
Start-up costs | USD/MW_e/start-up | 9750 | 9750 | 9750 | 9750 | 7500 | 15000 | 6750 | 12000 | M
Technology specific data
Water consumption | L/MWh | 2540 | 2540 | 2540 | 2540 | - | - | - | - |  | 15, 16, 17, 18, 19
Notes:
A | A two-unit configuration is typical in nuclear power plants, but more units can be combined.
B | Generation IV reactors are expected to achieve efficiencies well above 45 %. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency.
C | % of yearly hours with forced outage.
D | The construction time refers solely to the period from when the final investment decision (FID) is taken and until commercial operation. It does not include project preparation stages such as feasibility studies, site selection, licensing, or pre-construction activities, unless explicitly stated otherwise.
E | Nuclear power plants have a very' high energy' density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns.
F | The Russian VVER-1200-technology is used as a reference.
G | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
H | Decommissioning costs are usually 15% of the total investment cost, it is not included in the investment cost.
I | The specific investment breakdown is composed by 40% share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 45% of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and start-up costs), 12% of Owner's cost. Financial costs are excluded (would add around 20% to the investment cost).
J | The development of the overnight cost is based on NREL ATB 2024.
K | CAPEX shall reflect a potential first of a kind plant according to [9]. As limited data is available for these, specific cost information of recently and currently developed plants in various markets is consulted, spanning France, UK, China and the UAE [13], excluding data for Russia, South Korea and USA not being representative due to maturity of market, political and macroeconomic situations.
L | Uncertainty (Upper/Lower) is estimated as +/- 25 %.
M | Start-up costs are assumed to be 0.15% of CAPEX.
N | Based on Russian reactor technologies.
References
1 | NEA, 2023 - Technical and Economic Aspects of Load Following with Nuclear Power Plants. Nuclear Power Reactors in the World ¦ IAEA
2 | N. IEA, “Projected cost of generating electricity 2020 Edition,” Int. ENERGY AGENCY Nucl. ENERGY AGENCY Organ. Econ. CO-OPERATION Dev., no. January, p. 112, 2020, [Online]. Available: https://ncdc.gov.ng/themes/common/docs/protocols/111_1579986179.pdf
3 | US Dept. of Energy, Office of Nuclear Energy. The ultimate fast facts guide to Nuclear Energy
4 | STRATA, 2017 - The Footprint of Energy: Land use of US Electricity Production
5 | World Nuclear Association. Online: https: www.world-nuclear.org/infonnation-library/nuclear-fuel-cycle/nuclear-power-reactors/nuclear-power-reactors.aspx
6 | IEA-NEA, 2020 - Projected Costs of Generating Electricity
7 | NREL, 2024 - Annual Technology' Baseline 2024
8 | NEA, 2011 - Technical and Economic Aspects of Load Following with Nuclear Power Plants, Online: https://www.oecd-nea.org/upload/docs/application/pdf/2021-12/technical_and_economic_aspects_of_load_following_with_nuclear_power_plants.pdf
9 | O. NEA, 2020 - Unlocking Reductions in the Construction Costs of Nuclear: A Practical Guide for Stakeholders. doi: 10.1787/9789264303119-en
10 | Economics of Nuclear Power (Updated September 2023).Online: https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#CapitalCosts
11 | Lazard LCOE+, June 2025
12 | IEA, World Energy Outlook 2025, 2025
13 | Rystad Energy, 2024 - Global Nuclear Energy Review
14 | IAEA, 2025 - Power Reactor Information System. Online: https://pris.iaea.org/
15 | International Energy Agency, 2016 - Water Energy Nexus
16 | National Renewable Energy Laboratory, 2011 - A Review of Operational Water Consumption and Withdrawal Factors for Electricity Generating Technologies
17 | MME, UPME, DEA & Emergente, 2025 - Colombian Technology Catalogue for Power Generation and Storage Technologies 2025
18 | U.S. Department of Energy, Office of Nuclear Energy, 2023 - Updated Assessment of WaterEnergy Issues for Nuclear Power
19 | World resources institute, 2020 - Guidance for calculating water use embedded in purchased electricity

## Nuclear SMR
Nuclear SMR
Parameter | Unit | 2025 | 2030 | 2040 | 2050 | Uncertainty (2030) |  | Uncertainty (2050) |  | Note | Ref
[6 empty] | Lower | Upper | Lower | Upper
Energy/technical data
Generating capacity for one unit | MW_e | 100 | 100 | 100 | 100 | 80 | 125 |  |  |  | 1, 2, 3, 4
Generating capacity for total power plant | MW_e | 300 | 300 | 300 | 300 | [5 empty] | 1, 3, 4
Electrical efficiency, net, name plate | % | 33 | 34 | 35 | 36 |  |  |  |  | A | 1, 2
Electrical efficiency, net, annual average | % | 30 | 31 | 32 | 34 |  |  |  |  | A | 1, 2, 4, 5
Forced outage | % | 3 | 3 | 3 | 3 |  |  |  |  | B | 1, 4
Planned outage | % | 6.5 | 6 | 5.5 | 5 | 3 | 7 |  |  |  | 2
Self-consumption | % | 29 | 25 | 22 | 20 | 20 | 30 |  |  | I | 12
Technical lifetime | years | 40 | 45 | 50 | 55 | 30 | 60 |  |  |  | 2, 3
Construction time | years | 9 | 8 | 6 | 4 | 8 | 12 |  |  | C | 2, 3, 6
Space requirement | 1000_m2/MW_e | 0.64 | 0.64 | 0.64 | 0.64 | 0.05 | 1.6 | 0.05 | 1.6 | D | 1, 7
Additional data for non-thermal plants
Capacity factor, theoretical | % | - | - | - | - | - | - | - | -
Capacity factor, incl. outages | % | - | - | - | - | - | - | - | -
Ramping ability
Ramping | % of full load/minute | 1.2 | 1.2 | 1.2 | 1.2 |  |  |  |  | E
Minimum load | % of full load | 25 | 25 | 25 | 25 |  |  |  |  | E
Warm start-up time | hours | 1.5 | 1.5 | 1.5 | 1.5
Cold start-up time | hours | 24 | 24 | 24 | 24
Environment
PM 2.5 | g/GJ_i | -
SO2 (degree of desulphuring) | % | -
NOX | g/GJ_i | -
CH4 | g/GJ_i | -
N2O | g/GJ_i | -
Economic data (in USD2025)
Specific investment | MUSD/MW_e | - | 7.5 | 6 | 5 | 5 | 15 | 4 | 10 | F, G | 6, 9, 10, 11
- of which equipment | % | - | 33 | 33 | 33 | - | - | - | - | G
- of which installation and other costs | % | - | 67 | 67 | 67 | - | - | - | - | G
- of which equipment | MUSD/MW_e | - | 2.5 | 2 | 1.67 | 1.67 | 5 | 1.33 | 3.33 | G
- of which installation and other costs | MUSD/MW_e | - | 5 | 4 | 3.33 | 3.33 | 10 | 2.67 | 6.67 | G
Fixed O&M | USD/MW_e/year | - | 110000 | 105000 | 102000 | - | - | - | -
Variable O&M | USD/MWh | - | 2.2 | 2.15 | 2.1 | - | - | - | - | H | 2, 3, 8
Start-up costs | USD/MW_e/start-up | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
Water consumption | L/MWh | - | - | - | - | - | - | - | -
Notes:
A | Generation IV reactors are expected to achieve efficiencies well above 45 %. In the future, nuclear reactors are likely' to run often at partial load - thus the gap between nameplate and net efficiency.
B | % of yearly hours with forced outage.
C | = 109 months: China managed to connect its first SMR, one of two 100 MW HTR-PM reactors, to the grid on 20 December 2021. Construction began in 2012, and by then the time estimate for construction had increased to '50 months'. In reality, the first unit took almost 109 months from first concrete to mains connection, more than twice as long as expected.
D | Nuclear power plants have a 'high energy density' in terms of area required. The values represented here are for the area needed for the plants. However, there can be a higher requirement based on government regulation and environmental concerns.
E | Ramping and minimum load are constrained by the core stability'. Minimum requirements are usually set by the regulation.
F | Decommissioning costs usually are the 15% of the total investment cost.
G | The specific investment breakdown is composed by 40% share of direct cost (i.e., Equipment, Labour, Construction, Materials and Building), 45% of Indirect cost (i.e., Design services, Construction and Supervision and project management, Commissioning and start-up costs), 12% of Owner's cost. Financial costs are excluded (would add around 20% to the investment cost).
H | The main characteristics are taken from CAREM-25.
I | Based on reactor type HTR-PM. Other reactor types like ACP100, RITM-200N and NuScale all have a self-consumption rate around 20%.
References
1 | IAEA, 2024 - Small modular reactors: Advances in SMR developments, 2024. Online: https://www-pub.iaea.org/MTCD/Publications/PDF/p15790-PUB9062_web.pdf
2 | IAEA Nuclear Energy Series No. Nr-T-1.18 Technology Roadmap for small Modular Reactor Deployment, 2021- https://www-pub.iaea.org/MTCD/Publications/PDF/PUB1944_web.pdf
3 | M. A. Rahmanta, A. W. Harto, A. Agung, and M. K. Ridwan, “Nuclear Power Plant to Support Indonesia’s Net Zero Emissions: A Case Study of Small Modular Reactor Technology Selection Using Technology Readiness Level and Levelized Cost of Electricity Comparing Method,” Energies, vol. 16, no. 9, p. 3752, Apr. 2023
4 | Goswami GG, Rahman U, Chowdhury M. Estimating the economic cost of setting up a nuclear power plant at Rooppur in Bangladesh. Environ Sci Pollut Res Int. 2022 May;29(23):35073-35095. doi: 10.1007/s11356-021-18129-3. Epub 2022 Jan 19. PMID: 35044606; PMCID: PMC8767363
5 | WNA Word Nuclear Association, economics of Nuclear Power (Updated September 2023) - https://www.world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power.aspx#ECSArticleLink1
6 | Eye-popping new cost estimates released for NuScale small modular reactor, IEEFA, January 2023 - https://ieefa.org/resources/eye-popping-new-cost-estimates-released-nuscale-small-modular-reactor
7 | Giorgio Locatelli, Benito Mignacca, Small Modular Nuclear Reactors
8 | IEA, Nuclear Power in a Clean Energy System (2019) https://iea.blob.core.windows.net/assets/ad5a93ce-3a7f-461d-a441-8a05b7601887/Nuclear_Power_in_a_Clean_Energy_System.pdf
9 | NREL, 2025, Annual Technology Baseline
10 | S. Boarin, M. Mancini, M. Ricotti, G. Locatelli, Economics and financing of small modular reactors (SMRs)
11 | B. Mignacca, G. Locatelli, “Economics and finance of Small Modular Reactors: A systematic review and research agenda”, Renewable and Sustainable Energy Reviews (2020), (https://doi.org/10.1016/j.rser.2019.109519)
12 | IAEA, 2025 - Power Reactor Information System. Online: https://pris.iaea.org/